## Heat X-changer Worksheet
Air Cooled Heat Exchanger
| AIR |  |  |  | OIL |  | Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg 36-15, 27-11
Air |  |  |  | Air @ Elevation
Elevation |  |  | Elev = | 3345 | ft
Atmospheric Pressure at Elevation |  |  | Patm = | 13.0459 | psia
Temperature of the Air - Ambient |  |  | Tamb = | 100 | °F
|  | which is | Tamb = | 559.67 | °R
Molecular Weight of Air |  |  | MW = | 28.967 | lbm/lbmol |  | Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg 24-15
Universal Gas Constant |  |  | Ru = | 10.7316 | ft^3-lbf/lbmol-°R |  | Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg 24-14
Density of Air |  |  | p = | 0.062919 | lbm/ft^3 |  | Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg 24-14, pg A-14 inverse
Flow Rate of the Air |  |  | mair = | 17852 | ft^3/min
|  | which is | mair = | 67393.9648 | lbm/hr
Specific Heat of Air |  |  | Cpair = | 0.24 | btu/lbm-°R |  | Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg 24-15, A-94
Temperature of the Air going Out |  |  | Tout = | 133.6 | °F
Ambient Temperature - Temp going in |  |  | Tin = | 100 | °F
|  |  | ΔT = | 33.6 | °F
Heat Rate at Sea Level |  |  | Qair = | 659504.4078 | btu/hr | 193.281
Heat Rate at Site (Heat Taken Away from Oil) |  |  | Qair = | 543464.9323 | btu/hr | 159.2733
|  |  | difference from Sea Level = | -116039.4755 | btu/hr | -34.0077
Oil
Density of the Oil |  |  | p = | 861 | kg/m^3
|  | which is | p = | 7.1853 | lbm/gal
Flow Rate of the Oil |  |  | moil = | 173 | gpm
|  | which is | moil = | 74583.3843 | lbm/hr
Specific Heat of Oil |  |  | Cpoil = | 0.47264 | btu/lbm-°R
Temperature of the Oil Going In |  |  | Tin = | 179 | °F
Temperature of the Oil Going Out |  |  | Tout = | 150 | °F
|  |  | ΔT = | 29 | °F
Heat Rate (Heat Given to Air) |  |  | Qoil = | 1022281.6314 | btu/hr | 299.6001
|  |  | difference = | -478816.6991 | btu/hr | -140.3268
Amont Mixing Valve | [6 empty] | Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg 38-5, pg 38-6
Flow of Oil B Going Into Valve (Tank) |  |  | = | 74583.3843 | lbm/hr
Temperature of Oil B Going In (Tank) |  |  | Tb = | 157 | °F
Flow of Oil C Going Into Valve (Cooler) |  |  | = | 74583.3843 | lbm/hr
Temperature of Oil B Going Into Valve (Cooler) |  |  | Tc = | 150 | °F
Temperature of the Mixture |  |  | Tmix = | 153.5 | °F | *This is a loose estimate and can be off by up to 10°F due to valve friction, pressure drop, and different flow rates.
Sizing Comparison
Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg 20-9
Brake Horse Power of 1st Motor |  |  | BHP1 = | 4.7 | hp
Brake Horse Power of 2nd Motor |  |  | BHP2 = | 7 | hp
Speed of 1st Fan |  |  | n1 = | 1800 | rpm
Speed of 2nd Fan |  |  | n2 = | 2055.603 | rpm
Brake Horse Power of 1st Motor |  |  | BHP1 = | 4.7 | hp
Brake Horse Power of 2nd Motor |  |  | BHP2 = | 7 | hp
Flow of 1st Fan |  |  | Q1 = | 17852 | ft^3/min
Flow of 2nd Fan |  |  | Q2 = | 20387.0133 | ft^3/min
Flow of 1st Fan |  |  | Q1 = | 17852 | ft^3/min
Flow of 2nd Fan |  |  | Q2 = | 20387.01 | ft^3/min
Brake Horse Power of 1st Motor |  |  | BHP1 = | 4.7 | hp
Brake Horse Power of 2nd Motor |  |  | BHP2 = | 7 | hp
Flow of 1st Fan |  |  | Q1 = | 17852 | ft^3/min
Flow of 2nd Fan |  |  | Q2 = | 20387.01 | ft^3/min
Speed of 1st Fan |  |  | n1 = | 1800 | rpm
Speed of 2nd Fan |  |  | n2 = | 2055.6026 | rpm
Note on F12: Albany 269 ft Baker 3351 ft Boise 3200 ft Buhl 3345 ft Burley 4269 ft Caldwell 2497 ft Chehalis 470 ft Cisco 4400 ft Eugene 655 ft Goldendale 1712 ft Green River 6224 ft Kemmerer 6610 ft La Plata B 6643 ft Lava Hot Springs 4910 ft Little Valley 2889 ft McMinnville 185 ft Meacham 3780 ft Mesa 1050 ft Moab 5873 ft Mountain Home 3190 ft Mount Vernon 150 ft Muddy Creek 6855 ft Oregon City 170 ft Owyhee 5230 ft Pegram 6070 ft Pleasant View 7014 ft Plymouth 304 ft Pocatello 4655 ft Rangely 5500 ft Roosevelt 1220 ft Snohomish 466 ft Soda Springs 6135 ft Sumas 35 ft Sumner 456 ft Tumwater 110 ft Vernal 6008 ft Washougal 530 ft Willard 1280 ft Winchester 600 ft Zillah 1079 ft
Note on F13: Atmospheric Pressure Patm = 14.54(55096-(Elevation-361) ------------------------------ (55096+(Elevation-361) AGA, Part 3, pg 23
Note on F16: Gas Symbol MW Acetylene C2H2 26.038 Air 28.967 Ammonia NH3 17.032 Argon Ar 39.944 Butan C4H10 58.124 Carbon Diaxide CO2 44.011 Carbon Monoxide CO 28.011 Chlorine Cl2 70.910 Ethane C2H6 30.070 Ethylene C2H4 28.054 Freon CCl2F2 120.925 Helium He 4.003 Hydrogen H2 2.016 Hydrogen Sulfide H2S 34.082 Krypton Kr 83.800 Methane CH4 16.043 Neon Ne 20.183 Ntirogen N2 28.016 Nitric Oxide NO 30.008 Nitrous Oxide NO2 44.010 Octane Vapor C8H18 114.232 Oxygen O2 32.000 Propane C3H8 44.097 Sulfur Dioxide SO2 64.066 Water Vapor H20 18.160 Xenon Xe 131.300 Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg 24-15
Note on F19: Flow rate is dependent upon the Fan Blade size, pitch, and RPM. Density is accounted for up above. This comes from Manufacturer's Spec Sheet.
Note on F21: T Cp ( Btu/lbm-F ) 0 0.239 32 0.240 100 0.240 200 0.241 300 0.243 400 0.245 500 0.247 600 0.250 700 0.253 800 0.256 900 0.259 1000 0.262 1500 0.276 2000 0.286 2500 0.292 3000 0.297 Mechanical Engineering Reference Manual, Ed. 11, Lindeburg, pg A-94
Note on F25: Most Coolers are sized at Sea Level. 14.7 psia 60°F
Note on F30: Mobil SCH 824 Grade c32 = 861 kg/m^3 Mobil SCH 825 Grade c46 = 865 kg/m^3 Mobil Pegasus 701 Grade c40 = 885 kg/m^3 Mobil Pegasus 701 Grade c30 = 881 kg/m^3
Note on F32: In the case of Turbines, this flow rate can be approximated with %NGP. Meaning that not all the rated flow will be pumping through the coolers. But rather, a percentage of NGP. Example: 175 gpm * 97% NGP = 169.75 gpm
Note on F34: Typical Cp of Oil is approximately 0.45 to 0.53
OIL OUT
OIL B IN
AIR IN
AIR OUT
A
B
C
OIL C IN
OIL A OUT
OIL IN
SAMPLE

## LO ΔTemp
|  |  | Temperature of the Air going Out (from 1st Tab) | [6 empty] | Tout = | 133.6 | °F
Temperature Differential |  |  | Ambient Temperatures (Air In) | [97 empty] | Ambient Temperatures (Air In)
|  |  | -20 | -19 | -18 | -17 | -16 | -15 | -14 | -13 | -12 | -11 | -10 | -9 | -8 | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120
| Lube Oil Temps In | 180 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 179 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 178 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 177 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 176 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 175 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 174 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 173 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 172 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 171 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 170 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 169 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 168 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 167 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 166 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 165 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 164 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 163 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 162 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 161 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 160 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 159 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 158 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 157 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 156 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 155 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 154 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 153 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 152 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 151 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 150 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 149 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 148 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 147 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 146 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 145 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 144 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 143 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 142 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 141 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 140 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 139 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 138 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 137 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 136 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 135 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 134 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 133 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 132 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 131 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 130 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 129 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 128 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 127 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 126 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 125 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 124 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 123 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 122 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 121 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 120 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 119 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 118 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 117 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 116 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 115 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 114 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 113 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 112 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 111 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 110 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 109 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 108 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 107 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 106 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 105 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 104 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 103 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 102 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 101 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402
|  | 100 | 70.4776 | 70.0187 | 69.5599 | 69.1011 | 68.6422 | 68.1834 | 67.7245 | 67.2657 | 66.8069 | 66.348 | 65.8892 | 65.4303 | 64.9715 | 64.5127 | 64.0538 | 63.595 | 63.1362 | 62.6773 | 62.2185 | 61.7596 | 61.3008 | 60.842 | 60.3831 | 59.9243 | 59.4654 | 59.0066 | 58.5478 | 58.0889 | 57.6301 | 57.1713 | 56.7124 | 56.2536 | 55.7947 | 55.3359 | 54.8771 | 54.4182 | 53.9594 | 53.5005 | 53.0417 | 52.5829 | 52.124 | 51.6652 | 51.2064 | 50.7475 | 50.2887 | 49.8298 | 49.371 | 48.9122 | 48.4533 | 47.9945 | 47.5357 | 47.0768 | 46.618 | 46.1591 | 45.7003 | 45.2415 | 44.7826 | 44.3238 | 43.8649 | 43.4061 | 42.9473 | 42.4884 | 42.0296 | 41.5708 | 41.1119 | 40.6531 | 40.1942 | 39.7354 | 39.2766 | 38.8177 | 38.3589 | 37.9 | 37.4412 | 36.9824 | 36.5235 | 36.0647 | 35.6059 | 35.147 | 34.6882 | 34.2293 | 33.7705 | 33.3117 | 32.8528 | 32.394 | 31.9351 | 31.4763 | 31.0175 | 30.5586 | 30.0998 | 29.641 | 29.1821 | 28.7233 | 28.2644 | 27.8056 | 27.3468 | 26.8879 | 26.4291 | 25.9702 | 25.5114 | 25.0526 | 24.5937 | 24.1349 | 23.6761 | 23.2172 | 22.7584 | 22.2995 | 21.8407 | 21.3819 | 20.923 | 20.4642 | 20.0054 | 19.5465 | 19.0877 | 18.6288 | 18.17 | 17.7112 | 17.2523 | 16.7935 | 16.3346 | 15.8758 | 15.417 | 14.9581 | 14.4993 | 14.0405 | 13.5816 | 13.1228 | 12.6639 | 12.2051 | 11.7463 | 11.2874 | 10.8286 | 10.3697 | 9.9109 | 9.4521 | 8.9932 | 8.5344 | 8.0756 | 7.6167 | 7.1579 | 6.699 | 6.2402

## LO Temp Out
|  |  | Temperature of the Air going Out (from 1st Tab) | [6 empty] | Tout = | 133.6 | °F
Lube Oil Temps Out |  |  | Ambient Temperatures (Air In)
|  |  | -20 | -19 | -18 | -17 | -16 | -15 | -14 | -13 | -12 | -11 | -10 | -9 | -8 | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120
| Lube Oil Temps In | 180 | 109.5224 | 109.9813 | 110.4401 | 110.8989 | 111.3578 | 111.8166 | 112.2755 | 112.7343 | 113.1931 | 113.652 | 114.1108 | 114.5697 | 115.0285 | 115.4873 | 115.9462 | 116.405 | 116.8638 | 117.3227 | 117.7815 | 118.2404 | 118.6992 | 119.158 | 119.6169 | 120.0757 | 120.5346 | 120.9934 | 121.4522 | 121.9111 | 122.3699 | 122.8287 | 123.2876 | 123.7464 | 124.2053 | 124.6641 | 125.1229 | 125.5818 | 126.0406 | 126.4995 | 126.9583 | 127.4171 | 127.876 | 128.3348 | 128.7936 | 129.2525 | 129.7113 | 130.1702 | 130.629 | 131.0878 | 131.5467 | 132.0055 | 132.4643 | 132.9232 | 133.382 | 133.8409 | 134.2997 | 134.7585 | 135.2174 | 135.6762 | 136.1351 | 136.5939 | 137.0527 | 137.5116 | 137.9704 | 138.4292 | 138.8881 | 139.3469 | 139.8058 | 140.2646 | 140.7234 | 141.1823 | 141.6411 | 142.1 | 142.5588 | 143.0176 | 143.4765 | 143.9353 | 144.3941 | 144.853 | 145.3118 | 145.7707 | 146.2295 | 146.6883 | 147.1472 | 147.606 | 148.0649 | 148.5237 | 148.9825 | 149.4414 | 149.9002 | 150.359 | 150.8179 | 151.2767 | 151.7356 | 152.1944 | 152.6532 | 153.1121 | 153.5709 | 154.0298 | 154.4886 | 154.9474 | 155.4063 | 155.8651 | 156.3239 | 156.7828 | 157.2416 | 157.7005 | 158.1593 | 158.6181 | 159.077 | 159.5358 | 159.9946 | 160.4535 | 160.9123 | 161.3712 | 161.83 | 162.2888 | 162.7477 | 163.2065 | 163.6654 | 164.1242 | 164.583 | 165.0419 | 165.5007 | 165.9595 | 166.4184 | 166.8772 | 167.3361 | 167.7949 | 168.2537 | 168.7126 | 169.1714 | 169.6303 | 170.0891 | 170.5479 | 171.0068 | 171.4656 | 171.9244 | 172.3833 | 172.8421 | 173.301 | 173.7598
|  | 179 | 108.5224 | 108.9813 | 109.4401 | 109.8989 | 110.3578 | 110.8166 | 111.2755 | 111.7343 | 112.1931 | 112.652 | 113.1108 | 113.5697 | 114.0285 | 114.4873 | 114.9462 | 115.405 | 115.8638 | 116.3227 | 116.7815 | 117.2404 | 117.6992 | 118.158 | 118.6169 | 119.0757 | 119.5346 | 119.9934 | 120.4522 | 120.9111 | 121.3699 | 121.8287 | 122.2876 | 122.7464 | 123.2053 | 123.6641 | 124.1229 | 124.5818 | 125.0406 | 125.4995 | 125.9583 | 126.4171 | 126.876 | 127.3348 | 127.7936 | 128.2525 | 128.7113 | 129.1702 | 129.629 | 130.0878 | 130.5467 | 131.0055 | 131.4643 | 131.9232 | 132.382 | 132.8409 | 133.2997 | 133.7585 | 134.2174 | 134.6762 | 135.1351 | 135.5939 | 136.0527 | 136.5116 | 136.9704 | 137.4292 | 137.8881 | 138.3469 | 138.8058 | 139.2646 | 139.7234 | 140.1823 | 140.6411 | 141.1 | 141.5588 | 142.0176 | 142.4765 | 142.9353 | 143.3941 | 143.853 | 144.3118 | 144.7707 | 145.2295 | 145.6883 | 146.1472 | 146.606 | 147.0649 | 147.5237 | 147.9825 | 148.4414 | 148.9002 | 149.359 | 149.8179 | 150.2767 | 150.7356 | 151.1944 | 151.6532 | 152.1121 | 152.5709 | 153.0298 | 153.4886 | 153.9474 | 154.4063 | 154.8651 | 155.3239 | 155.7828 | 156.2416 | 156.7005 | 157.1593 | 157.6181 | 158.077 | 158.5358 | 158.9946 | 159.4535 | 159.9123 | 160.3712 | 160.83 | 161.2888 | 161.7477 | 162.2065 | 162.6654 | 163.1242 | 163.583 | 164.0419 | 164.5007 | 164.9595 | 165.4184 | 165.8772 | 166.3361 | 166.7949 | 167.2537 | 167.7126 | 168.1714 | 168.6303 | 169.0891 | 169.5479 | 170.0068 | 170.4656 | 170.9244 | 171.3833 | 171.8421 | 172.301 | 172.7598
|  | 178 | 107.5224 | 107.9813 | 108.4401 | 108.8989 | 109.3578 | 109.8166 | 110.2755 | 110.7343 | 111.1931 | 111.652 | 112.1108 | 112.5697 | 113.0285 | 113.4873 | 113.9462 | 114.405 | 114.8638 | 115.3227 | 115.7815 | 116.2404 | 116.6992 | 117.158 | 117.6169 | 118.0757 | 118.5346 | 118.9934 | 119.4522 | 119.9111 | 120.3699 | 120.8287 | 121.2876 | 121.7464 | 122.2053 | 122.6641 | 123.1229 | 123.5818 | 124.0406 | 124.4995 | 124.9583 | 125.4171 | 125.876 | 126.3348 | 126.7936 | 127.2525 | 127.7113 | 128.1702 | 128.629 | 129.0878 | 129.5467 | 130.0055 | 130.4643 | 130.9232 | 131.382 | 131.8409 | 132.2997 | 132.7585 | 133.2174 | 133.6762 | 134.1351 | 134.5939 | 135.0527 | 135.5116 | 135.9704 | 136.4292 | 136.8881 | 137.3469 | 137.8058 | 138.2646 | 138.7234 | 139.1823 | 139.6411 | 140.1 | 140.5588 | 141.0176 | 141.4765 | 141.9353 | 142.3941 | 142.853 | 143.3118 | 143.7707 | 144.2295 | 144.6883 | 145.1472 | 145.606 | 146.0649 | 146.5237 | 146.9825 | 147.4414 | 147.9002 | 148.359 | 148.8179 | 149.2767 | 149.7356 | 150.1944 | 150.6532 | 151.1121 | 151.5709 | 152.0298 | 152.4886 | 152.9474 | 153.4063 | 153.8651 | 154.3239 | 154.7828 | 155.2416 | 155.7005 | 156.1593 | 156.6181 | 157.077 | 157.5358 | 157.9946 | 158.4535 | 158.9123 | 159.3712 | 159.83 | 160.2888 | 160.7477 | 161.2065 | 161.6654 | 162.1242 | 162.583 | 163.0419 | 163.5007 | 163.9595 | 164.4184 | 164.8772 | 165.3361 | 165.7949 | 166.2537 | 166.7126 | 167.1714 | 167.6303 | 168.0891 | 168.5479 | 169.0068 | 169.4656 | 169.9244 | 170.3833 | 170.8421 | 171.301 | 171.7598
|  | 177 | 106.5224 | 106.9813 | 107.4401 | 107.8989 | 108.3578 | 108.8166 | 109.2755 | 109.7343 | 110.1931 | 110.652 | 111.1108 | 111.5697 | 112.0285 | 112.4873 | 112.9462 | 113.405 | 113.8638 | 114.3227 | 114.7815 | 115.2404 | 115.6992 | 116.158 | 116.6169 | 117.0757 | 117.5346 | 117.9934 | 118.4522 | 118.9111 | 119.3699 | 119.8287 | 120.2876 | 120.7464 | 121.2053 | 121.6641 | 122.1229 | 122.5818 | 123.0406 | 123.4995 | 123.9583 | 124.4171 | 124.876 | 125.3348 | 125.7936 | 126.2525 | 126.7113 | 127.1702 | 127.629 | 128.0878 | 128.5467 | 129.0055 | 129.4643 | 129.9232 | 130.382 | 130.8409 | 131.2997 | 131.7585 | 132.2174 | 132.6762 | 133.1351 | 133.5939 | 134.0527 | 134.5116 | 134.9704 | 135.4292 | 135.8881 | 136.3469 | 136.8058 | 137.2646 | 137.7234 | 138.1823 | 138.6411 | 139.1 | 139.5588 | 140.0176 | 140.4765 | 140.9353 | 141.3941 | 141.853 | 142.3118 | 142.7707 | 143.2295 | 143.6883 | 144.1472 | 144.606 | 145.0649 | 145.5237 | 145.9825 | 146.4414 | 146.9002 | 147.359 | 147.8179 | 148.2767 | 148.7356 | 149.1944 | 149.6532 | 150.1121 | 150.5709 | 151.0298 | 151.4886 | 151.9474 | 152.4063 | 152.8651 | 153.3239 | 153.7828 | 154.2416 | 154.7005 | 155.1593 | 155.6181 | 156.077 | 156.5358 | 156.9946 | 157.4535 | 157.9123 | 158.3712 | 158.83 | 159.2888 | 159.7477 | 160.2065 | 160.6654 | 161.1242 | 161.583 | 162.0419 | 162.5007 | 162.9595 | 163.4184 | 163.8772 | 164.3361 | 164.7949 | 165.2537 | 165.7126 | 166.1714 | 166.6303 | 167.0891 | 167.5479 | 168.0068 | 168.4656 | 168.9244 | 169.3833 | 169.8421 | 170.301 | 170.7598
|  | 176 | 105.5224 | 105.9813 | 106.4401 | 106.8989 | 107.3578 | 107.8166 | 108.2755 | 108.7343 | 109.1931 | 109.652 | 110.1108 | 110.5697 | 111.0285 | 111.4873 | 111.9462 | 112.405 | 112.8638 | 113.3227 | 113.7815 | 114.2404 | 114.6992 | 115.158 | 115.6169 | 116.0757 | 116.5346 | 116.9934 | 117.4522 | 117.9111 | 118.3699 | 118.8287 | 119.2876 | 119.7464 | 120.2053 | 120.6641 | 121.1229 | 121.5818 | 122.0406 | 122.4995 | 122.9583 | 123.4171 | 123.876 | 124.3348 | 124.7936 | 125.2525 | 125.7113 | 126.1702 | 126.629 | 127.0878 | 127.5467 | 128.0055 | 128.4643 | 128.9232 | 129.382 | 129.8409 | 130.2997 | 130.7585 | 131.2174 | 131.6762 | 132.1351 | 132.5939 | 133.0527 | 133.5116 | 133.9704 | 134.4292 | 134.8881 | 135.3469 | 135.8058 | 136.2646 | 136.7234 | 137.1823 | 137.6411 | 138.1 | 138.5588 | 139.0176 | 139.4765 | 139.9353 | 140.3941 | 140.853 | 141.3118 | 141.7707 | 142.2295 | 142.6883 | 143.1472 | 143.606 | 144.0649 | 144.5237 | 144.9825 | 145.4414 | 145.9002 | 146.359 | 146.8179 | 147.2767 | 147.7356 | 148.1944 | 148.6532 | 149.1121 | 149.5709 | 150.0298 | 150.4886 | 150.9474 | 151.4063 | 151.8651 | 152.3239 | 152.7828 | 153.2416 | 153.7005 | 154.1593 | 154.6181 | 155.077 | 155.5358 | 155.9946 | 156.4535 | 156.9123 | 157.3712 | 157.83 | 158.2888 | 158.7477 | 159.2065 | 159.6654 | 160.1242 | 160.583 | 161.0419 | 161.5007 | 161.9595 | 162.4184 | 162.8772 | 163.3361 | 163.7949 | 164.2537 | 164.7126 | 165.1714 | 165.6303 | 166.0891 | 166.5479 | 167.0068 | 167.4656 | 167.9244 | 168.3833 | 168.8421 | 169.301 | 169.7598
|  | 175 | 104.5224 | 104.9813 | 105.4401 | 105.8989 | 106.3578 | 106.8166 | 107.2755 | 107.7343 | 108.1931 | 108.652 | 109.1108 | 109.5697 | 110.0285 | 110.4873 | 110.9462 | 111.405 | 111.8638 | 112.3227 | 112.7815 | 113.2404 | 113.6992 | 114.158 | 114.6169 | 115.0757 | 115.5346 | 115.9934 | 116.4522 | 116.9111 | 117.3699 | 117.8287 | 118.2876 | 118.7464 | 119.2053 | 119.6641 | 120.1229 | 120.5818 | 121.0406 | 121.4995 | 121.9583 | 122.4171 | 122.876 | 123.3348 | 123.7936 | 124.2525 | 124.7113 | 125.1702 | 125.629 | 126.0878 | 126.5467 | 127.0055 | 127.4643 | 127.9232 | 128.382 | 128.8409 | 129.2997 | 129.7585 | 130.2174 | 130.6762 | 131.1351 | 131.5939 | 132.0527 | 132.5116 | 132.9704 | 133.4292 | 133.8881 | 134.3469 | 134.8058 | 135.2646 | 135.7234 | 136.1823 | 136.6411 | 137.1 | 137.5588 | 138.0176 | 138.4765 | 138.9353 | 139.3941 | 139.853 | 140.3118 | 140.7707 | 141.2295 | 141.6883 | 142.1472 | 142.606 | 143.0649 | 143.5237 | 143.9825 | 144.4414 | 144.9002 | 145.359 | 145.8179 | 146.2767 | 146.7356 | 147.1944 | 147.6532 | 148.1121 | 148.5709 | 149.0298 | 149.4886 | 149.9474 | 150.4063 | 150.8651 | 151.3239 | 151.7828 | 152.2416 | 152.7005 | 153.1593 | 153.6181 | 154.077 | 154.5358 | 154.9946 | 155.4535 | 155.9123 | 156.3712 | 156.83 | 157.2888 | 157.7477 | 158.2065 | 158.6654 | 159.1242 | 159.583 | 160.0419 | 160.5007 | 160.9595 | 161.4184 | 161.8772 | 162.3361 | 162.7949 | 163.2537 | 163.7126 | 164.1714 | 164.6303 | 165.0891 | 165.5479 | 166.0068 | 166.4656 | 166.9244 | 167.3833 | 167.8421 | 168.301 | 168.7598
|  | 174 | 103.5224 | 103.9813 | 104.4401 | 104.8989 | 105.3578 | 105.8166 | 106.2755 | 106.7343 | 107.1931 | 107.652 | 108.1108 | 108.5697 | 109.0285 | 109.4873 | 109.9462 | 110.405 | 110.8638 | 111.3227 | 111.7815 | 112.2404 | 112.6992 | 113.158 | 113.6169 | 114.0757 | 114.5346 | 114.9934 | 115.4522 | 115.9111 | 116.3699 | 116.8287 | 117.2876 | 117.7464 | 118.2053 | 118.6641 | 119.1229 | 119.5818 | 120.0406 | 120.4995 | 120.9583 | 121.4171 | 121.876 | 122.3348 | 122.7936 | 123.2525 | 123.7113 | 124.1702 | 124.629 | 125.0878 | 125.5467 | 126.0055 | 126.4643 | 126.9232 | 127.382 | 127.8409 | 128.2997 | 128.7585 | 129.2174 | 129.6762 | 130.1351 | 130.5939 | 131.0527 | 131.5116 | 131.9704 | 132.4292 | 132.8881 | 133.3469 | 133.8058 | 134.2646 | 134.7234 | 135.1823 | 135.6411 | 136.1 | 136.5588 | 137.0176 | 137.4765 | 137.9353 | 138.3941 | 138.853 | 139.3118 | 139.7707 | 140.2295 | 140.6883 | 141.1472 | 141.606 | 142.0649 | 142.5237 | 142.9825 | 143.4414 | 143.9002 | 144.359 | 144.8179 | 145.2767 | 145.7356 | 146.1944 | 146.6532 | 147.1121 | 147.5709 | 148.0298 | 148.4886 | 148.9474 | 149.4063 | 149.8651 | 150.3239 | 150.7828 | 151.2416 | 151.7005 | 152.1593 | 152.6181 | 153.077 | 153.5358 | 153.9946 | 154.4535 | 154.9123 | 155.3712 | 155.83 | 156.2888 | 156.7477 | 157.2065 | 157.6654 | 158.1242 | 158.583 | 159.0419 | 159.5007 | 159.9595 | 160.4184 | 160.8772 | 161.3361 | 161.7949 | 162.2537 | 162.7126 | 163.1714 | 163.6303 | 164.0891 | 164.5479 | 165.0068 | 165.4656 | 165.9244 | 166.3833 | 166.8421 | 167.301 | 167.7598
|  | 173 | 102.5224 | 102.9813 | 103.4401 | 103.8989 | 104.3578 | 104.8166 | 105.2755 | 105.7343 | 106.1931 | 106.652 | 107.1108 | 107.5697 | 108.0285 | 108.4873 | 108.9462 | 109.405 | 109.8638 | 110.3227 | 110.7815 | 111.2404 | 111.6992 | 112.158 | 112.6169 | 113.0757 | 113.5346 | 113.9934 | 114.4522 | 114.9111 | 115.3699 | 115.8287 | 116.2876 | 116.7464 | 117.2053 | 117.6641 | 118.1229 | 118.5818 | 119.0406 | 119.4995 | 119.9583 | 120.4171 | 120.876 | 121.3348 | 121.7936 | 122.2525 | 122.7113 | 123.1702 | 123.629 | 124.0878 | 124.5467 | 125.0055 | 125.4643 | 125.9232 | 126.382 | 126.8409 | 127.2997 | 127.7585 | 128.2174 | 128.6762 | 129.1351 | 129.5939 | 130.0527 | 130.5116 | 130.9704 | 131.4292 | 131.8881 | 132.3469 | 132.8058 | 133.2646 | 133.7234 | 134.1823 | 134.6411 | 135.1 | 135.5588 | 136.0176 | 136.4765 | 136.9353 | 137.3941 | 137.853 | 138.3118 | 138.7707 | 139.2295 | 139.6883 | 140.1472 | 140.606 | 141.0649 | 141.5237 | 141.9825 | 142.4414 | 142.9002 | 143.359 | 143.8179 | 144.2767 | 144.7356 | 145.1944 | 145.6532 | 146.1121 | 146.5709 | 147.0298 | 147.4886 | 147.9474 | 148.4063 | 148.8651 | 149.3239 | 149.7828 | 150.2416 | 150.7005 | 151.1593 | 151.6181 | 152.077 | 152.5358 | 152.9946 | 153.4535 | 153.9123 | 154.3712 | 154.83 | 155.2888 | 155.7477 | 156.2065 | 156.6654 | 157.1242 | 157.583 | 158.0419 | 158.5007 | 158.9595 | 159.4184 | 159.8772 | 160.3361 | 160.7949 | 161.2537 | 161.7126 | 162.1714 | 162.6303 | 163.0891 | 163.5479 | 164.0068 | 164.4656 | 164.9244 | 165.3833 | 165.8421 | 166.301 | 166.7598
|  | 172 | 101.5224 | 101.9813 | 102.4401 | 102.8989 | 103.3578 | 103.8166 | 104.2755 | 104.7343 | 105.1931 | 105.652 | 106.1108 | 106.5697 | 107.0285 | 107.4873 | 107.9462 | 108.405 | 108.8638 | 109.3227 | 109.7815 | 110.2404 | 110.6992 | 111.158 | 111.6169 | 112.0757 | 112.5346 | 112.9934 | 113.4522 | 113.9111 | 114.3699 | 114.8287 | 115.2876 | 115.7464 | 116.2053 | 116.6641 | 117.1229 | 117.5818 | 118.0406 | 118.4995 | 118.9583 | 119.4171 | 119.876 | 120.3348 | 120.7936 | 121.2525 | 121.7113 | 122.1702 | 122.629 | 123.0878 | 123.5467 | 124.0055 | 124.4643 | 124.9232 | 125.382 | 125.8409 | 126.2997 | 126.7585 | 127.2174 | 127.6762 | 128.1351 | 128.5939 | 129.0527 | 129.5116 | 129.9704 | 130.4292 | 130.8881 | 131.3469 | 131.8058 | 132.2646 | 132.7234 | 133.1823 | 133.6411 | 134.1 | 134.5588 | 135.0176 | 135.4765 | 135.9353 | 136.3941 | 136.853 | 137.3118 | 137.7707 | 138.2295 | 138.6883 | 139.1472 | 139.606 | 140.0649 | 140.5237 | 140.9825 | 141.4414 | 141.9002 | 142.359 | 142.8179 | 143.2767 | 143.7356 | 144.1944 | 144.6532 | 145.1121 | 145.5709 | 146.0298 | 146.4886 | 146.9474 | 147.4063 | 147.8651 | 148.3239 | 148.7828 | 149.2416 | 149.7005 | 150.1593 | 150.6181 | 151.077 | 151.5358 | 151.9946 | 152.4535 | 152.9123 | 153.3712 | 153.83 | 154.2888 | 154.7477 | 155.2065 | 155.6654 | 156.1242 | 156.583 | 157.0419 | 157.5007 | 157.9595 | 158.4184 | 158.8772 | 159.3361 | 159.7949 | 160.2537 | 160.7126 | 161.1714 | 161.6303 | 162.0891 | 162.5479 | 163.0068 | 163.4656 | 163.9244 | 164.3833 | 164.8421 | 165.301 | 165.7598
|  | 171 | 100.5224 | 100.9813 | 101.4401 | 101.8989 | 102.3578 | 102.8166 | 103.2755 | 103.7343 | 104.1931 | 104.652 | 105.1108 | 105.5697 | 106.0285 | 106.4873 | 106.9462 | 107.405 | 107.8638 | 108.3227 | 108.7815 | 109.2404 | 109.6992 | 110.158 | 110.6169 | 111.0757 | 111.5346 | 111.9934 | 112.4522 | 112.9111 | 113.3699 | 113.8287 | 114.2876 | 114.7464 | 115.2053 | 115.6641 | 116.1229 | 116.5818 | 117.0406 | 117.4995 | 117.9583 | 118.4171 | 118.876 | 119.3348 | 119.7936 | 120.2525 | 120.7113 | 121.1702 | 121.629 | 122.0878 | 122.5467 | 123.0055 | 123.4643 | 123.9232 | 124.382 | 124.8409 | 125.2997 | 125.7585 | 126.2174 | 126.6762 | 127.1351 | 127.5939 | 128.0527 | 128.5116 | 128.9704 | 129.4292 | 129.8881 | 130.3469 | 130.8058 | 131.2646 | 131.7234 | 132.1823 | 132.6411 | 133.1 | 133.5588 | 134.0176 | 134.4765 | 134.9353 | 135.3941 | 135.853 | 136.3118 | 136.7707 | 137.2295 | 137.6883 | 138.1472 | 138.606 | 139.0649 | 139.5237 | 139.9825 | 140.4414 | 140.9002 | 141.359 | 141.8179 | 142.2767 | 142.7356 | 143.1944 | 143.6532 | 144.1121 | 144.5709 | 145.0298 | 145.4886 | 145.9474 | 146.4063 | 146.8651 | 147.3239 | 147.7828 | 148.2416 | 148.7005 | 149.1593 | 149.6181 | 150.077 | 150.5358 | 150.9946 | 151.4535 | 151.9123 | 152.3712 | 152.83 | 153.2888 | 153.7477 | 154.2065 | 154.6654 | 155.1242 | 155.583 | 156.0419 | 156.5007 | 156.9595 | 157.4184 | 157.8772 | 158.3361 | 158.7949 | 159.2537 | 159.7126 | 160.1714 | 160.6303 | 161.0891 | 161.5479 | 162.0068 | 162.4656 | 162.9244 | 163.3833 | 163.8421 | 164.301 | 164.7598
|  | 170 | 99.5224 | 99.9813 | 100.4401 | 100.8989 | 101.3578 | 101.8166 | 102.2755 | 102.7343 | 103.1931 | 103.652 | 104.1108 | 104.5697 | 105.0285 | 105.4873 | 105.9462 | 106.405 | 106.8638 | 107.3227 | 107.7815 | 108.2404 | 108.6992 | 109.158 | 109.6169 | 110.0757 | 110.5346 | 110.9934 | 111.4522 | 111.9111 | 112.3699 | 112.8287 | 113.2876 | 113.7464 | 114.2053 | 114.6641 | 115.1229 | 115.5818 | 116.0406 | 116.4995 | 116.9583 | 117.4171 | 117.876 | 118.3348 | 118.7936 | 119.2525 | 119.7113 | 120.1702 | 120.629 | 121.0878 | 121.5467 | 122.0055 | 122.4643 | 122.9232 | 123.382 | 123.8409 | 124.2997 | 124.7585 | 125.2174 | 125.6762 | 126.1351 | 126.5939 | 127.0527 | 127.5116 | 127.9704 | 128.4292 | 128.8881 | 129.3469 | 129.8058 | 130.2646 | 130.7234 | 131.1823 | 131.6411 | 132.1 | 132.5588 | 133.0176 | 133.4765 | 133.9353 | 134.3941 | 134.853 | 135.3118 | 135.7707 | 136.2295 | 136.6883 | 137.1472 | 137.606 | 138.0649 | 138.5237 | 138.9825 | 139.4414 | 139.9002 | 140.359 | 140.8179 | 141.2767 | 141.7356 | 142.1944 | 142.6532 | 143.1121 | 143.5709 | 144.0298 | 144.4886 | 144.9474 | 145.4063 | 145.8651 | 146.3239 | 146.7828 | 147.2416 | 147.7005 | 148.1593 | 148.6181 | 149.077 | 149.5358 | 149.9946 | 150.4535 | 150.9123 | 151.3712 | 151.83 | 152.2888 | 152.7477 | 153.2065 | 153.6654 | 154.1242 | 154.583 | 155.0419 | 155.5007 | 155.9595 | 156.4184 | 156.8772 | 157.3361 | 157.7949 | 158.2537 | 158.7126 | 159.1714 | 159.6303 | 160.0891 | 160.5479 | 161.0068 | 161.4656 | 161.9244 | 162.3833 | 162.8421 | 163.301 | 163.7598
|  | 169 | 98.5224 | 98.9813 | 99.4401 | 99.8989 | 100.3578 | 100.8166 | 101.2755 | 101.7343 | 102.1931 | 102.652 | 103.1108 | 103.5697 | 104.0285 | 104.4873 | 104.9462 | 105.405 | 105.8638 | 106.3227 | 106.7815 | 107.2404 | 107.6992 | 108.158 | 108.6169 | 109.0757 | 109.5346 | 109.9934 | 110.4522 | 110.9111 | 111.3699 | 111.8287 | 112.2876 | 112.7464 | 113.2053 | 113.6641 | 114.1229 | 114.5818 | 115.0406 | 115.4995 | 115.9583 | 116.4171 | 116.876 | 117.3348 | 117.7936 | 118.2525 | 118.7113 | 119.1702 | 119.629 | 120.0878 | 120.5467 | 121.0055 | 121.4643 | 121.9232 | 122.382 | 122.8409 | 123.2997 | 123.7585 | 124.2174 | 124.6762 | 125.1351 | 125.5939 | 126.0527 | 126.5116 | 126.9704 | 127.4292 | 127.8881 | 128.3469 | 128.8058 | 129.2646 | 129.7234 | 130.1823 | 130.6411 | 131.1 | 131.5588 | 132.0176 | 132.4765 | 132.9353 | 133.3941 | 133.853 | 134.3118 | 134.7707 | 135.2295 | 135.6883 | 136.1472 | 136.606 | 137.0649 | 137.5237 | 137.9825 | 138.4414 | 138.9002 | 139.359 | 139.8179 | 140.2767 | 140.7356 | 141.1944 | 141.6532 | 142.1121 | 142.5709 | 143.0298 | 143.4886 | 143.9474 | 144.4063 | 144.8651 | 145.3239 | 145.7828 | 146.2416 | 146.7005 | 147.1593 | 147.6181 | 148.077 | 148.5358 | 148.9946 | 149.4535 | 149.9123 | 150.3712 | 150.83 | 151.2888 | 151.7477 | 152.2065 | 152.6654 | 153.1242 | 153.583 | 154.0419 | 154.5007 | 154.9595 | 155.4184 | 155.8772 | 156.3361 | 156.7949 | 157.2537 | 157.7126 | 158.1714 | 158.6303 | 159.0891 | 159.5479 | 160.0068 | 160.4656 | 160.9244 | 161.3833 | 161.8421 | 162.301 | 162.7598
|  | 168 | 97.5224 | 97.9813 | 98.4401 | 98.8989 | 99.3578 | 99.8166 | 100.2755 | 100.7343 | 101.1931 | 101.652 | 102.1108 | 102.5697 | 103.0285 | 103.4873 | 103.9462 | 104.405 | 104.8638 | 105.3227 | 105.7815 | 106.2404 | 106.6992 | 107.158 | 107.6169 | 108.0757 | 108.5346 | 108.9934 | 109.4522 | 109.9111 | 110.3699 | 110.8287 | 111.2876 | 111.7464 | 112.2053 | 112.6641 | 113.1229 | 113.5818 | 114.0406 | 114.4995 | 114.9583 | 115.4171 | 115.876 | 116.3348 | 116.7936 | 117.2525 | 117.7113 | 118.1702 | 118.629 | 119.0878 | 119.5467 | 120.0055 | 120.4643 | 120.9232 | 121.382 | 121.8409 | 122.2997 | 122.7585 | 123.2174 | 123.6762 | 124.1351 | 124.5939 | 125.0527 | 125.5116 | 125.9704 | 126.4292 | 126.8881 | 127.3469 | 127.8058 | 128.2646 | 128.7234 | 129.1823 | 129.6411 | 130.1 | 130.5588 | 131.0176 | 131.4765 | 131.9353 | 132.3941 | 132.853 | 133.3118 | 133.7707 | 134.2295 | 134.6883 | 135.1472 | 135.606 | 136.0649 | 136.5237 | 136.9825 | 137.4414 | 137.9002 | 138.359 | 138.8179 | 139.2767 | 139.7356 | 140.1944 | 140.6532 | 141.1121 | 141.5709 | 142.0298 | 142.4886 | 142.9474 | 143.4063 | 143.8651 | 144.3239 | 144.7828 | 145.2416 | 145.7005 | 146.1593 | 146.6181 | 147.077 | 147.5358 | 147.9946 | 148.4535 | 148.9123 | 149.3712 | 149.83 | 150.2888 | 150.7477 | 151.2065 | 151.6654 | 152.1242 | 152.583 | 153.0419 | 153.5007 | 153.9595 | 154.4184 | 154.8772 | 155.3361 | 155.7949 | 156.2537 | 156.7126 | 157.1714 | 157.6303 | 158.0891 | 158.5479 | 159.0068 | 159.4656 | 159.9244 | 160.3833 | 160.8421 | 161.301 | 161.7598
|  | 167 | 96.5224 | 96.9813 | 97.4401 | 97.8989 | 98.3578 | 98.8166 | 99.2755 | 99.7343 | 100.1931 | 100.652 | 101.1108 | 101.5697 | 102.0285 | 102.4873 | 102.9462 | 103.405 | 103.8638 | 104.3227 | 104.7815 | 105.2404 | 105.6992 | 106.158 | 106.6169 | 107.0757 | 107.5346 | 107.9934 | 108.4522 | 108.9111 | 109.3699 | 109.8287 | 110.2876 | 110.7464 | 111.2053 | 111.6641 | 112.1229 | 112.5818 | 113.0406 | 113.4995 | 113.9583 | 114.4171 | 114.876 | 115.3348 | 115.7936 | 116.2525 | 116.7113 | 117.1702 | 117.629 | 118.0878 | 118.5467 | 119.0055 | 119.4643 | 119.9232 | 120.382 | 120.8409 | 121.2997 | 121.7585 | 122.2174 | 122.6762 | 123.1351 | 123.5939 | 124.0527 | 124.5116 | 124.9704 | 125.4292 | 125.8881 | 126.3469 | 126.8058 | 127.2646 | 127.7234 | 128.1823 | 128.6411 | 129.1 | 129.5588 | 130.0176 | 130.4765 | 130.9353 | 131.3941 | 131.853 | 132.3118 | 132.7707 | 133.2295 | 133.6883 | 134.1472 | 134.606 | 135.0649 | 135.5237 | 135.9825 | 136.4414 | 136.9002 | 137.359 | 137.8179 | 138.2767 | 138.7356 | 139.1944 | 139.6532 | 140.1121 | 140.5709 | 141.0298 | 141.4886 | 141.9474 | 142.4063 | 142.8651 | 143.3239 | 143.7828 | 144.2416 | 144.7005 | 145.1593 | 145.6181 | 146.077 | 146.5358 | 146.9946 | 147.4535 | 147.9123 | 148.3712 | 148.83 | 149.2888 | 149.7477 | 150.2065 | 150.6654 | 151.1242 | 151.583 | 152.0419 | 152.5007 | 152.9595 | 153.4184 | 153.8772 | 154.3361 | 154.7949 | 155.2537 | 155.7126 | 156.1714 | 156.6303 | 157.0891 | 157.5479 | 158.0068 | 158.4656 | 158.9244 | 159.3833 | 159.8421 | 160.301 | 160.7598
|  | 166 | 95.5224 | 95.9813 | 96.4401 | 96.8989 | 97.3578 | 97.8166 | 98.2755 | 98.7343 | 99.1931 | 99.652 | 100.1108 | 100.5697 | 101.0285 | 101.4873 | 101.9462 | 102.405 | 102.8638 | 103.3227 | 103.7815 | 104.2404 | 104.6992 | 105.158 | 105.6169 | 106.0757 | 106.5346 | 106.9934 | 107.4522 | 107.9111 | 108.3699 | 108.8287 | 109.2876 | 109.7464 | 110.2053 | 110.6641 | 111.1229 | 111.5818 | 112.0406 | 112.4995 | 112.9583 | 113.4171 | 113.876 | 114.3348 | 114.7936 | 115.2525 | 115.7113 | 116.1702 | 116.629 | 117.0878 | 117.5467 | 118.0055 | 118.4643 | 118.9232 | 119.382 | 119.8409 | 120.2997 | 120.7585 | 121.2174 | 121.6762 | 122.1351 | 122.5939 | 123.0527 | 123.5116 | 123.9704 | 124.4292 | 124.8881 | 125.3469 | 125.8058 | 126.2646 | 126.7234 | 127.1823 | 127.6411 | 128.1 | 128.5588 | 129.0176 | 129.4765 | 129.9353 | 130.3941 | 130.853 | 131.3118 | 131.7707 | 132.2295 | 132.6883 | 133.1472 | 133.606 | 134.0649 | 134.5237 | 134.9825 | 135.4414 | 135.9002 | 136.359 | 136.8179 | 137.2767 | 137.7356 | 138.1944 | 138.6532 | 139.1121 | 139.5709 | 140.0298 | 140.4886 | 140.9474 | 141.4063 | 141.8651 | 142.3239 | 142.7828 | 143.2416 | 143.7005 | 144.1593 | 144.6181 | 145.077 | 145.5358 | 145.9946 | 146.4535 | 146.9123 | 147.3712 | 147.83 | 148.2888 | 148.7477 | 149.2065 | 149.6654 | 150.1242 | 150.583 | 151.0419 | 151.5007 | 151.9595 | 152.4184 | 152.8772 | 153.3361 | 153.7949 | 154.2537 | 154.7126 | 155.1714 | 155.6303 | 156.0891 | 156.5479 | 157.0068 | 157.4656 | 157.9244 | 158.3833 | 158.8421 | 159.301 | 159.7598
|  | 165 | 94.5224 | 94.9813 | 95.4401 | 95.8989 | 96.3578 | 96.8166 | 97.2755 | 97.7343 | 98.1931 | 98.652 | 99.1108 | 99.5697 | 100.0285 | 100.4873 | 100.9462 | 101.405 | 101.8638 | 102.3227 | 102.7815 | 103.2404 | 103.6992 | 104.158 | 104.6169 | 105.0757 | 105.5346 | 105.9934 | 106.4522 | 106.9111 | 107.3699 | 107.8287 | 108.2876 | 108.7464 | 109.2053 | 109.6641 | 110.1229 | 110.5818 | 111.0406 | 111.4995 | 111.9583 | 112.4171 | 112.876 | 113.3348 | 113.7936 | 114.2525 | 114.7113 | 115.1702 | 115.629 | 116.0878 | 116.5467 | 117.0055 | 117.4643 | 117.9232 | 118.382 | 118.8409 | 119.2997 | 119.7585 | 120.2174 | 120.6762 | 121.1351 | 121.5939 | 122.0527 | 122.5116 | 122.9704 | 123.4292 | 123.8881 | 124.3469 | 124.8058 | 125.2646 | 125.7234 | 126.1823 | 126.6411 | 127.1 | 127.5588 | 128.0176 | 128.4765 | 128.9353 | 129.3941 | 129.853 | 130.3118 | 130.7707 | 131.2295 | 131.6883 | 132.1472 | 132.606 | 133.0649 | 133.5237 | 133.9825 | 134.4414 | 134.9002 | 135.359 | 135.8179 | 136.2767 | 136.7356 | 137.1944 | 137.6532 | 138.1121 | 138.5709 | 139.0298 | 139.4886 | 139.9474 | 140.4063 | 140.8651 | 141.3239 | 141.7828 | 142.2416 | 142.7005 | 143.1593 | 143.6181 | 144.077 | 144.5358 | 144.9946 | 145.4535 | 145.9123 | 146.3712 | 146.83 | 147.2888 | 147.7477 | 148.2065 | 148.6654 | 149.1242 | 149.583 | 150.0419 | 150.5007 | 150.9595 | 151.4184 | 151.8772 | 152.3361 | 152.7949 | 153.2537 | 153.7126 | 154.1714 | 154.6303 | 155.0891 | 155.5479 | 156.0068 | 156.4656 | 156.9244 | 157.3833 | 157.8421 | 158.301 | 158.7598
|  | 164 | 93.5224 | 93.9813 | 94.4401 | 94.8989 | 95.3578 | 95.8166 | 96.2755 | 96.7343 | 97.1931 | 97.652 | 98.1108 | 98.5697 | 99.0285 | 99.4873 | 99.9462 | 100.405 | 100.8638 | 101.3227 | 101.7815 | 102.2404 | 102.6992 | 103.158 | 103.6169 | 104.0757 | 104.5346 | 104.9934 | 105.4522 | 105.9111 | 106.3699 | 106.8287 | 107.2876 | 107.7464 | 108.2053 | 108.6641 | 109.1229 | 109.5818 | 110.0406 | 110.4995 | 110.9583 | 111.4171 | 111.876 | 112.3348 | 112.7936 | 113.2525 | 113.7113 | 114.1702 | 114.629 | 115.0878 | 115.5467 | 116.0055 | 116.4643 | 116.9232 | 117.382 | 117.8409 | 118.2997 | 118.7585 | 119.2174 | 119.6762 | 120.1351 | 120.5939 | 121.0527 | 121.5116 | 121.9704 | 122.4292 | 122.8881 | 123.3469 | 123.8058 | 124.2646 | 124.7234 | 125.1823 | 125.6411 | 126.1 | 126.5588 | 127.0176 | 127.4765 | 127.9353 | 128.3941 | 128.853 | 129.3118 | 129.7707 | 130.2295 | 130.6883 | 131.1472 | 131.606 | 132.0649 | 132.5237 | 132.9825 | 133.4414 | 133.9002 | 134.359 | 134.8179 | 135.2767 | 135.7356 | 136.1944 | 136.6532 | 137.1121 | 137.5709 | 138.0298 | 138.4886 | 138.9474 | 139.4063 | 139.8651 | 140.3239 | 140.7828 | 141.2416 | 141.7005 | 142.1593 | 142.6181 | 143.077 | 143.5358 | 143.9946 | 144.4535 | 144.9123 | 145.3712 | 145.83 | 146.2888 | 146.7477 | 147.2065 | 147.6654 | 148.1242 | 148.583 | 149.0419 | 149.5007 | 149.9595 | 150.4184 | 150.8772 | 151.3361 | 151.7949 | 152.2537 | 152.7126 | 153.1714 | 153.6303 | 154.0891 | 154.5479 | 155.0068 | 155.4656 | 155.9244 | 156.3833 | 156.8421 | 157.301 | 157.7598
|  | 163 | 92.5224 | 92.9813 | 93.4401 | 93.8989 | 94.3578 | 94.8166 | 95.2755 | 95.7343 | 96.1931 | 96.652 | 97.1108 | 97.5697 | 98.0285 | 98.4873 | 98.9462 | 99.405 | 99.8638 | 100.3227 | 100.7815 | 101.2404 | 101.6992 | 102.158 | 102.6169 | 103.0757 | 103.5346 | 103.9934 | 104.4522 | 104.9111 | 105.3699 | 105.8287 | 106.2876 | 106.7464 | 107.2053 | 107.6641 | 108.1229 | 108.5818 | 109.0406 | 109.4995 | 109.9583 | 110.4171 | 110.876 | 111.3348 | 111.7936 | 112.2525 | 112.7113 | 113.1702 | 113.629 | 114.0878 | 114.5467 | 115.0055 | 115.4643 | 115.9232 | 116.382 | 116.8409 | 117.2997 | 117.7585 | 118.2174 | 118.6762 | 119.1351 | 119.5939 | 120.0527 | 120.5116 | 120.9704 | 121.4292 | 121.8881 | 122.3469 | 122.8058 | 123.2646 | 123.7234 | 124.1823 | 124.6411 | 125.1 | 125.5588 | 126.0176 | 126.4765 | 126.9353 | 127.3941 | 127.853 | 128.3118 | 128.7707 | 129.2295 | 129.6883 | 130.1472 | 130.606 | 131.0649 | 131.5237 | 131.9825 | 132.4414 | 132.9002 | 133.359 | 133.8179 | 134.2767 | 134.7356 | 135.1944 | 135.6532 | 136.1121 | 136.5709 | 137.0298 | 137.4886 | 137.9474 | 138.4063 | 138.8651 | 139.3239 | 139.7828 | 140.2416 | 140.7005 | 141.1593 | 141.6181 | 142.077 | 142.5358 | 142.9946 | 143.4535 | 143.9123 | 144.3712 | 144.83 | 145.2888 | 145.7477 | 146.2065 | 146.6654 | 147.1242 | 147.583 | 148.0419 | 148.5007 | 148.9595 | 149.4184 | 149.8772 | 150.3361 | 150.7949 | 151.2537 | 151.7126 | 152.1714 | 152.6303 | 153.0891 | 153.5479 | 154.0068 | 154.4656 | 154.9244 | 155.3833 | 155.8421 | 156.301 | 156.7598
|  | 162 | 91.5224 | 91.9813 | 92.4401 | 92.8989 | 93.3578 | 93.8166 | 94.2755 | 94.7343 | 95.1931 | 95.652 | 96.1108 | 96.5697 | 97.0285 | 97.4873 | 97.9462 | 98.405 | 98.8638 | 99.3227 | 99.7815 | 100.2404 | 100.6992 | 101.158 | 101.6169 | 102.0757 | 102.5346 | 102.9934 | 103.4522 | 103.9111 | 104.3699 | 104.8287 | 105.2876 | 105.7464 | 106.2053 | 106.6641 | 107.1229 | 107.5818 | 108.0406 | 108.4995 | 108.9583 | 109.4171 | 109.876 | 110.3348 | 110.7936 | 111.2525 | 111.7113 | 112.1702 | 112.629 | 113.0878 | 113.5467 | 114.0055 | 114.4643 | 114.9232 | 115.382 | 115.8409 | 116.2997 | 116.7585 | 117.2174 | 117.6762 | 118.1351 | 118.5939 | 119.0527 | 119.5116 | 119.9704 | 120.4292 | 120.8881 | 121.3469 | 121.8058 | 122.2646 | 122.7234 | 123.1823 | 123.6411 | 124.1 | 124.5588 | 125.0176 | 125.4765 | 125.9353 | 126.3941 | 126.853 | 127.3118 | 127.7707 | 128.2295 | 128.6883 | 129.1472 | 129.606 | 130.0649 | 130.5237 | 130.9825 | 131.4414 | 131.9002 | 132.359 | 132.8179 | 133.2767 | 133.7356 | 134.1944 | 134.6532 | 135.1121 | 135.5709 | 136.0298 | 136.4886 | 136.9474 | 137.4063 | 137.8651 | 138.3239 | 138.7828 | 139.2416 | 139.7005 | 140.1593 | 140.6181 | 141.077 | 141.5358 | 141.9946 | 142.4535 | 142.9123 | 143.3712 | 143.83 | 144.2888 | 144.7477 | 145.2065 | 145.6654 | 146.1242 | 146.583 | 147.0419 | 147.5007 | 147.9595 | 148.4184 | 148.8772 | 149.3361 | 149.7949 | 150.2537 | 150.7126 | 151.1714 | 151.6303 | 152.0891 | 152.5479 | 153.0068 | 153.4656 | 153.9244 | 154.3833 | 154.8421 | 155.301 | 155.7598
|  | 161 | 90.5224 | 90.9813 | 91.4401 | 91.8989 | 92.3578 | 92.8166 | 93.2755 | 93.7343 | 94.1931 | 94.652 | 95.1108 | 95.5697 | 96.0285 | 96.4873 | 96.9462 | 97.405 | 97.8638 | 98.3227 | 98.7815 | 99.2404 | 99.6992 | 100.158 | 100.6169 | 101.0757 | 101.5346 | 101.9934 | 102.4522 | 102.9111 | 103.3699 | 103.8287 | 104.2876 | 104.7464 | 105.2053 | 105.6641 | 106.1229 | 106.5818 | 107.0406 | 107.4995 | 107.9583 | 108.4171 | 108.876 | 109.3348 | 109.7936 | 110.2525 | 110.7113 | 111.1702 | 111.629 | 112.0878 | 112.5467 | 113.0055 | 113.4643 | 113.9232 | 114.382 | 114.8409 | 115.2997 | 115.7585 | 116.2174 | 116.6762 | 117.1351 | 117.5939 | 118.0527 | 118.5116 | 118.9704 | 119.4292 | 119.8881 | 120.3469 | 120.8058 | 121.2646 | 121.7234 | 122.1823 | 122.6411 | 123.1 | 123.5588 | 124.0176 | 124.4765 | 124.9353 | 125.3941 | 125.853 | 126.3118 | 126.7707 | 127.2295 | 127.6883 | 128.1472 | 128.606 | 129.0649 | 129.5237 | 129.9825 | 130.4414 | 130.9002 | 131.359 | 131.8179 | 132.2767 | 132.7356 | 133.1944 | 133.6532 | 134.1121 | 134.5709 | 135.0298 | 135.4886 | 135.9474 | 136.4063 | 136.8651 | 137.3239 | 137.7828 | 138.2416 | 138.7005 | 139.1593 | 139.6181 | 140.077 | 140.5358 | 140.9946 | 141.4535 | 141.9123 | 142.3712 | 142.83 | 143.2888 | 143.7477 | 144.2065 | 144.6654 | 145.1242 | 145.583 | 146.0419 | 146.5007 | 146.9595 | 147.4184 | 147.8772 | 148.3361 | 148.7949 | 149.2537 | 149.7126 | 150.1714 | 150.6303 | 151.0891 | 151.5479 | 152.0068 | 152.4656 | 152.9244 | 153.3833 | 153.8421 | 154.301 | 154.7598
|  | 160 | 89.5224 | 89.9813 | 90.4401 | 90.8989 | 91.3578 | 91.8166 | 92.2755 | 92.7343 | 93.1931 | 93.652 | 94.1108 | 94.5697 | 95.0285 | 95.4873 | 95.9462 | 96.405 | 96.8638 | 97.3227 | 97.7815 | 98.2404 | 98.6992 | 99.158 | 99.6169 | 100.0757 | 100.5346 | 100.9934 | 101.4522 | 101.9111 | 102.3699 | 102.8287 | 103.2876 | 103.7464 | 104.2053 | 104.6641 | 105.1229 | 105.5818 | 106.0406 | 106.4995 | 106.9583 | 107.4171 | 107.876 | 108.3348 | 108.7936 | 109.2525 | 109.7113 | 110.1702 | 110.629 | 111.0878 | 111.5467 | 112.0055 | 112.4643 | 112.9232 | 113.382 | 113.8409 | 114.2997 | 114.7585 | 115.2174 | 115.6762 | 116.1351 | 116.5939 | 117.0527 | 117.5116 | 117.9704 | 118.4292 | 118.8881 | 119.3469 | 119.8058 | 120.2646 | 120.7234 | 121.1823 | 121.6411 | 122.1 | 122.5588 | 123.0176 | 123.4765 | 123.9353 | 124.3941 | 124.853 | 125.3118 | 125.7707 | 126.2295 | 126.6883 | 127.1472 | 127.606 | 128.0649 | 128.5237 | 128.9825 | 129.4414 | 129.9002 | 130.359 | 130.8179 | 131.2767 | 131.7356 | 132.1944 | 132.6532 | 133.1121 | 133.5709 | 134.0298 | 134.4886 | 134.9474 | 135.4063 | 135.8651 | 136.3239 | 136.7828 | 137.2416 | 137.7005 | 138.1593 | 138.6181 | 139.077 | 139.5358 | 139.9946 | 140.4535 | 140.9123 | 141.3712 | 141.83 | 142.2888 | 142.7477 | 143.2065 | 143.6654 | 144.1242 | 144.583 | 145.0419 | 145.5007 | 145.9595 | 146.4184 | 146.8772 | 147.3361 | 147.7949 | 148.2537 | 148.7126 | 149.1714 | 149.6303 | 150.0891 | 150.5479 | 151.0068 | 151.4656 | 151.9244 | 152.3833 | 152.8421 | 153.301 | 153.7598
|  | 159 | 88.5224 | 88.9813 | 89.4401 | 89.8989 | 90.3578 | 90.8166 | 91.2755 | 91.7343 | 92.1931 | 92.652 | 93.1108 | 93.5697 | 94.0285 | 94.4873 | 94.9462 | 95.405 | 95.8638 | 96.3227 | 96.7815 | 97.2404 | 97.6992 | 98.158 | 98.6169 | 99.0757 | 99.5346 | 99.9934 | 100.4522 | 100.9111 | 101.3699 | 101.8287 | 102.2876 | 102.7464 | 103.2053 | 103.6641 | 104.1229 | 104.5818 | 105.0406 | 105.4995 | 105.9583 | 106.4171 | 106.876 | 107.3348 | 107.7936 | 108.2525 | 108.7113 | 109.1702 | 109.629 | 110.0878 | 110.5467 | 111.0055 | 111.4643 | 111.9232 | 112.382 | 112.8409 | 113.2997 | 113.7585 | 114.2174 | 114.6762 | 115.1351 | 115.5939 | 116.0527 | 116.5116 | 116.9704 | 117.4292 | 117.8881 | 118.3469 | 118.8058 | 119.2646 | 119.7234 | 120.1823 | 120.6411 | 121.1 | 121.5588 | 122.0176 | 122.4765 | 122.9353 | 123.3941 | 123.853 | 124.3118 | 124.7707 | 125.2295 | 125.6883 | 126.1472 | 126.606 | 127.0649 | 127.5237 | 127.9825 | 128.4414 | 128.9002 | 129.359 | 129.8179 | 130.2767 | 130.7356 | 131.1944 | 131.6532 | 132.1121 | 132.5709 | 133.0298 | 133.4886 | 133.9474 | 134.4063 | 134.8651 | 135.3239 | 135.7828 | 136.2416 | 136.7005 | 137.1593 | 137.6181 | 138.077 | 138.5358 | 138.9946 | 139.4535 | 139.9123 | 140.3712 | 140.83 | 141.2888 | 141.7477 | 142.2065 | 142.6654 | 143.1242 | 143.583 | 144.0419 | 144.5007 | 144.9595 | 145.4184 | 145.8772 | 146.3361 | 146.7949 | 147.2537 | 147.7126 | 148.1714 | 148.6303 | 149.0891 | 149.5479 | 150.0068 | 150.4656 | 150.9244 | 151.3833 | 151.8421 | 152.301 | 152.7598
|  | 158 | 87.5224 | 87.9813 | 88.4401 | 88.8989 | 89.3578 | 89.8166 | 90.2755 | 90.7343 | 91.1931 | 91.652 | 92.1108 | 92.5697 | 93.0285 | 93.4873 | 93.9462 | 94.405 | 94.8638 | 95.3227 | 95.7815 | 96.2404 | 96.6992 | 97.158 | 97.6169 | 98.0757 | 98.5346 | 98.9934 | 99.4522 | 99.9111 | 100.3699 | 100.8287 | 101.2876 | 101.7464 | 102.2053 | 102.6641 | 103.1229 | 103.5818 | 104.0406 | 104.4995 | 104.9583 | 105.4171 | 105.876 | 106.3348 | 106.7936 | 107.2525 | 107.7113 | 108.1702 | 108.629 | 109.0878 | 109.5467 | 110.0055 | 110.4643 | 110.9232 | 111.382 | 111.8409 | 112.2997 | 112.7585 | 113.2174 | 113.6762 | 114.1351 | 114.5939 | 115.0527 | 115.5116 | 115.9704 | 116.4292 | 116.8881 | 117.3469 | 117.8058 | 118.2646 | 118.7234 | 119.1823 | 119.6411 | 120.1 | 120.5588 | 121.0176 | 121.4765 | 121.9353 | 122.3941 | 122.853 | 123.3118 | 123.7707 | 124.2295 | 124.6883 | 125.1472 | 125.606 | 126.0649 | 126.5237 | 126.9825 | 127.4414 | 127.9002 | 128.359 | 128.8179 | 129.2767 | 129.7356 | 130.1944 | 130.6532 | 131.1121 | 131.5709 | 132.0298 | 132.4886 | 132.9474 | 133.4063 | 133.8651 | 134.3239 | 134.7828 | 135.2416 | 135.7005 | 136.1593 | 136.6181 | 137.077 | 137.5358 | 137.9946 | 138.4535 | 138.9123 | 139.3712 | 139.83 | 140.2888 | 140.7477 | 141.2065 | 141.6654 | 142.1242 | 142.583 | 143.0419 | 143.5007 | 143.9595 | 144.4184 | 144.8772 | 145.3361 | 145.7949 | 146.2537 | 146.7126 | 147.1714 | 147.6303 | 148.0891 | 148.5479 | 149.0068 | 149.4656 | 149.9244 | 150.3833 | 150.8421 | 151.301 | 151.7598
|  | 157 | 86.5224 | 86.9813 | 87.4401 | 87.8989 | 88.3578 | 88.8166 | 89.2755 | 89.7343 | 90.1931 | 90.652 | 91.1108 | 91.5697 | 92.0285 | 92.4873 | 92.9462 | 93.405 | 93.8638 | 94.3227 | 94.7815 | 95.2404 | 95.6992 | 96.158 | 96.6169 | 97.0757 | 97.5346 | 97.9934 | 98.4522 | 98.9111 | 99.3699 | 99.8287 | 100.2876 | 100.7464 | 101.2053 | 101.6641 | 102.1229 | 102.5818 | 103.0406 | 103.4995 | 103.9583 | 104.4171 | 104.876 | 105.3348 | 105.7936 | 106.2525 | 106.7113 | 107.1702 | 107.629 | 108.0878 | 108.5467 | 109.0055 | 109.4643 | 109.9232 | 110.382 | 110.8409 | 111.2997 | 111.7585 | 112.2174 | 112.6762 | 113.1351 | 113.5939 | 114.0527 | 114.5116 | 114.9704 | 115.4292 | 115.8881 | 116.3469 | 116.8058 | 117.2646 | 117.7234 | 118.1823 | 118.6411 | 119.1 | 119.5588 | 120.0176 | 120.4765 | 120.9353 | 121.3941 | 121.853 | 122.3118 | 122.7707 | 123.2295 | 123.6883 | 124.1472 | 124.606 | 125.0649 | 125.5237 | 125.9825 | 126.4414 | 126.9002 | 127.359 | 127.8179 | 128.2767 | 128.7356 | 129.1944 | 129.6532 | 130.1121 | 130.5709 | 131.0298 | 131.4886 | 131.9474 | 132.4063 | 132.8651 | 133.3239 | 133.7828 | 134.2416 | 134.7005 | 135.1593 | 135.6181 | 136.077 | 136.5358 | 136.9946 | 137.4535 | 137.9123 | 138.3712 | 138.83 | 139.2888 | 139.7477 | 140.2065 | 140.6654 | 141.1242 | 141.583 | 142.0419 | 142.5007 | 142.9595 | 143.4184 | 143.8772 | 144.3361 | 144.7949 | 145.2537 | 145.7126 | 146.1714 | 146.6303 | 147.0891 | 147.5479 | 148.0068 | 148.4656 | 148.9244 | 149.3833 | 149.8421 | 150.301 | 150.7598
|  | 156 | 85.5224 | 85.9813 | 86.4401 | 86.8989 | 87.3578 | 87.8166 | 88.2755 | 88.7343 | 89.1931 | 89.652 | 90.1108 | 90.5697 | 91.0285 | 91.4873 | 91.9462 | 92.405 | 92.8638 | 93.3227 | 93.7815 | 94.2404 | 94.6992 | 95.158 | 95.6169 | 96.0757 | 96.5346 | 96.9934 | 97.4522 | 97.9111 | 98.3699 | 98.8287 | 99.2876 | 99.7464 | 100.2053 | 100.6641 | 101.1229 | 101.5818 | 102.0406 | 102.4995 | 102.9583 | 103.4171 | 103.876 | 104.3348 | 104.7936 | 105.2525 | 105.7113 | 106.1702 | 106.629 | 107.0878 | 107.5467 | 108.0055 | 108.4643 | 108.9232 | 109.382 | 109.8409 | 110.2997 | 110.7585 | 111.2174 | 111.6762 | 112.1351 | 112.5939 | 113.0527 | 113.5116 | 113.9704 | 114.4292 | 114.8881 | 115.3469 | 115.8058 | 116.2646 | 116.7234 | 117.1823 | 117.6411 | 118.1 | 118.5588 | 119.0176 | 119.4765 | 119.9353 | 120.3941 | 120.853 | 121.3118 | 121.7707 | 122.2295 | 122.6883 | 123.1472 | 123.606 | 124.0649 | 124.5237 | 124.9825 | 125.4414 | 125.9002 | 126.359 | 126.8179 | 127.2767 | 127.7356 | 128.1944 | 128.6532 | 129.1121 | 129.5709 | 130.0298 | 130.4886 | 130.9474 | 131.4063 | 131.8651 | 132.3239 | 132.7828 | 133.2416 | 133.7005 | 134.1593 | 134.6181 | 135.077 | 135.5358 | 135.9946 | 136.4535 | 136.9123 | 137.3712 | 137.83 | 138.2888 | 138.7477 | 139.2065 | 139.6654 | 140.1242 | 140.583 | 141.0419 | 141.5007 | 141.9595 | 142.4184 | 142.8772 | 143.3361 | 143.7949 | 144.2537 | 144.7126 | 145.1714 | 145.6303 | 146.0891 | 146.5479 | 147.0068 | 147.4656 | 147.9244 | 148.3833 | 148.8421 | 149.301 | 149.7598
|  | 155 | 84.5224 | 84.9813 | 85.4401 | 85.8989 | 86.3578 | 86.8166 | 87.2755 | 87.7343 | 88.1931 | 88.652 | 89.1108 | 89.5697 | 90.0285 | 90.4873 | 90.9462 | 91.405 | 91.8638 | 92.3227 | 92.7815 | 93.2404 | 93.6992 | 94.158 | 94.6169 | 95.0757 | 95.5346 | 95.9934 | 96.4522 | 96.9111 | 97.3699 | 97.8287 | 98.2876 | 98.7464 | 99.2053 | 99.6641 | 100.1229 | 100.5818 | 101.0406 | 101.4995 | 101.9583 | 102.4171 | 102.876 | 103.3348 | 103.7936 | 104.2525 | 104.7113 | 105.1702 | 105.629 | 106.0878 | 106.5467 | 107.0055 | 107.4643 | 107.9232 | 108.382 | 108.8409 | 109.2997 | 109.7585 | 110.2174 | 110.6762 | 111.1351 | 111.5939 | 112.0527 | 112.5116 | 112.9704 | 113.4292 | 113.8881 | 114.3469 | 114.8058 | 115.2646 | 115.7234 | 116.1823 | 116.6411 | 117.1 | 117.5588 | 118.0176 | 118.4765 | 118.9353 | 119.3941 | 119.853 | 120.3118 | 120.7707 | 121.2295 | 121.6883 | 122.1472 | 122.606 | 123.0649 | 123.5237 | 123.9825 | 124.4414 | 124.9002 | 125.359 | 125.8179 | 126.2767 | 126.7356 | 127.1944 | 127.6532 | 128.1121 | 128.5709 | 129.0298 | 129.4886 | 129.9474 | 130.4063 | 130.8651 | 131.3239 | 131.7828 | 132.2416 | 132.7005 | 133.1593 | 133.6181 | 134.077 | 134.5358 | 134.9946 | 135.4535 | 135.9123 | 136.3712 | 136.83 | 137.2888 | 137.7477 | 138.2065 | 138.6654 | 139.1242 | 139.583 | 140.0419 | 140.5007 | 140.9595 | 141.4184 | 141.8772 | 142.3361 | 142.7949 | 143.2537 | 143.7126 | 144.1714 | 144.6303 | 145.0891 | 145.5479 | 146.0068 | 146.4656 | 146.9244 | 147.3833 | 147.8421 | 148.301 | 148.7598
|  | 154 | 83.5224 | 83.9813 | 84.4401 | 84.8989 | 85.3578 | 85.8166 | 86.2755 | 86.7343 | 87.1931 | 87.652 | 88.1108 | 88.5697 | 89.0285 | 89.4873 | 89.9462 | 90.405 | 90.8638 | 91.3227 | 91.7815 | 92.2404 | 92.6992 | 93.158 | 93.6169 | 94.0757 | 94.5346 | 94.9934 | 95.4522 | 95.9111 | 96.3699 | 96.8287 | 97.2876 | 97.7464 | 98.2053 | 98.6641 | 99.1229 | 99.5818 | 100.0406 | 100.4995 | 100.9583 | 101.4171 | 101.876 | 102.3348 | 102.7936 | 103.2525 | 103.7113 | 104.1702 | 104.629 | 105.0878 | 105.5467 | 106.0055 | 106.4643 | 106.9232 | 107.382 | 107.8409 | 108.2997 | 108.7585 | 109.2174 | 109.6762 | 110.1351 | 110.5939 | 111.0527 | 111.5116 | 111.9704 | 112.4292 | 112.8881 | 113.3469 | 113.8058 | 114.2646 | 114.7234 | 115.1823 | 115.6411 | 116.1 | 116.5588 | 117.0176 | 117.4765 | 117.9353 | 118.3941 | 118.853 | 119.3118 | 119.7707 | 120.2295 | 120.6883 | 121.1472 | 121.606 | 122.0649 | 122.5237 | 122.9825 | 123.4414 | 123.9002 | 124.359 | 124.8179 | 125.2767 | 125.7356 | 126.1944 | 126.6532 | 127.1121 | 127.5709 | 128.0298 | 128.4886 | 128.9474 | 129.4063 | 129.8651 | 130.3239 | 130.7828 | 131.2416 | 131.7005 | 132.1593 | 132.6181 | 133.077 | 133.5358 | 133.9946 | 134.4535 | 134.9123 | 135.3712 | 135.83 | 136.2888 | 136.7477 | 137.2065 | 137.6654 | 138.1242 | 138.583 | 139.0419 | 139.5007 | 139.9595 | 140.4184 | 140.8772 | 141.3361 | 141.7949 | 142.2537 | 142.7126 | 143.1714 | 143.6303 | 144.0891 | 144.5479 | 145.0068 | 145.4656 | 145.9244 | 146.3833 | 146.8421 | 147.301 | 147.7598
|  | 153 | 82.5224 | 82.9813 | 83.4401 | 83.8989 | 84.3578 | 84.8166 | 85.2755 | 85.7343 | 86.1931 | 86.652 | 87.1108 | 87.5697 | 88.0285 | 88.4873 | 88.9462 | 89.405 | 89.8638 | 90.3227 | 90.7815 | 91.2404 | 91.6992 | 92.158 | 92.6169 | 93.0757 | 93.5346 | 93.9934 | 94.4522 | 94.9111 | 95.3699 | 95.8287 | 96.2876 | 96.7464 | 97.2053 | 97.6641 | 98.1229 | 98.5818 | 99.0406 | 99.4995 | 99.9583 | 100.4171 | 100.876 | 101.3348 | 101.7936 | 102.2525 | 102.7113 | 103.1702 | 103.629 | 104.0878 | 104.5467 | 105.0055 | 105.4643 | 105.9232 | 106.382 | 106.8409 | 107.2997 | 107.7585 | 108.2174 | 108.6762 | 109.1351 | 109.5939 | 110.0527 | 110.5116 | 110.9704 | 111.4292 | 111.8881 | 112.3469 | 112.8058 | 113.2646 | 113.7234 | 114.1823 | 114.6411 | 115.1 | 115.5588 | 116.0176 | 116.4765 | 116.9353 | 117.3941 | 117.853 | 118.3118 | 118.7707 | 119.2295 | 119.6883 | 120.1472 | 120.606 | 121.0649 | 121.5237 | 121.9825 | 122.4414 | 122.9002 | 123.359 | 123.8179 | 124.2767 | 124.7356 | 125.1944 | 125.6532 | 126.1121 | 126.5709 | 127.0298 | 127.4886 | 127.9474 | 128.4063 | 128.8651 | 129.3239 | 129.7828 | 130.2416 | 130.7005 | 131.1593 | 131.6181 | 132.077 | 132.5358 | 132.9946 | 133.4535 | 133.9123 | 134.3712 | 134.83 | 135.2888 | 135.7477 | 136.2065 | 136.6654 | 137.1242 | 137.583 | 138.0419 | 138.5007 | 138.9595 | 139.4184 | 139.8772 | 140.3361 | 140.7949 | 141.2537 | 141.7126 | 142.1714 | 142.6303 | 143.0891 | 143.5479 | 144.0068 | 144.4656 | 144.9244 | 145.3833 | 145.8421 | 146.301 | 146.7598
|  | 152 | 81.5224 | 81.9813 | 82.4401 | 82.8989 | 83.3578 | 83.8166 | 84.2755 | 84.7343 | 85.1931 | 85.652 | 86.1108 | 86.5697 | 87.0285 | 87.4873 | 87.9462 | 88.405 | 88.8638 | 89.3227 | 89.7815 | 90.2404 | 90.6992 | 91.158 | 91.6169 | 92.0757 | 92.5346 | 92.9934 | 93.4522 | 93.9111 | 94.3699 | 94.8287 | 95.2876 | 95.7464 | 96.2053 | 96.6641 | 97.1229 | 97.5818 | 98.0406 | 98.4995 | 98.9583 | 99.4171 | 99.876 | 100.3348 | 100.7936 | 101.2525 | 101.7113 | 102.1702 | 102.629 | 103.0878 | 103.5467 | 104.0055 | 104.4643 | 104.9232 | 105.382 | 105.8409 | 106.2997 | 106.7585 | 107.2174 | 107.6762 | 108.1351 | 108.5939 | 109.0527 | 109.5116 | 109.9704 | 110.4292 | 110.8881 | 111.3469 | 111.8058 | 112.2646 | 112.7234 | 113.1823 | 113.6411 | 114.1 | 114.5588 | 115.0176 | 115.4765 | 115.9353 | 116.3941 | 116.853 | 117.3118 | 117.7707 | 118.2295 | 118.6883 | 119.1472 | 119.606 | 120.0649 | 120.5237 | 120.9825 | 121.4414 | 121.9002 | 122.359 | 122.8179 | 123.2767 | 123.7356 | 124.1944 | 124.6532 | 125.1121 | 125.5709 | 126.0298 | 126.4886 | 126.9474 | 127.4063 | 127.8651 | 128.3239 | 128.7828 | 129.2416 | 129.7005 | 130.1593 | 130.6181 | 131.077 | 131.5358 | 131.9946 | 132.4535 | 132.9123 | 133.3712 | 133.83 | 134.2888 | 134.7477 | 135.2065 | 135.6654 | 136.1242 | 136.583 | 137.0419 | 137.5007 | 137.9595 | 138.4184 | 138.8772 | 139.3361 | 139.7949 | 140.2537 | 140.7126 | 141.1714 | 141.6303 | 142.0891 | 142.5479 | 143.0068 | 143.4656 | 143.9244 | 144.3833 | 144.8421 | 145.301 | 145.7598
|  | 151 | 80.5224 | 80.9813 | 81.4401 | 81.8989 | 82.3578 | 82.8166 | 83.2755 | 83.7343 | 84.1931 | 84.652 | 85.1108 | 85.5697 | 86.0285 | 86.4873 | 86.9462 | 87.405 | 87.8638 | 88.3227 | 88.7815 | 89.2404 | 89.6992 | 90.158 | 90.6169 | 91.0757 | 91.5346 | 91.9934 | 92.4522 | 92.9111 | 93.3699 | 93.8287 | 94.2876 | 94.7464 | 95.2053 | 95.6641 | 96.1229 | 96.5818 | 97.0406 | 97.4995 | 97.9583 | 98.4171 | 98.876 | 99.3348 | 99.7936 | 100.2525 | 100.7113 | 101.1702 | 101.629 | 102.0878 | 102.5467 | 103.0055 | 103.4643 | 103.9232 | 104.382 | 104.8409 | 105.2997 | 105.7585 | 106.2174 | 106.6762 | 107.1351 | 107.5939 | 108.0527 | 108.5116 | 108.9704 | 109.4292 | 109.8881 | 110.3469 | 110.8058 | 111.2646 | 111.7234 | 112.1823 | 112.6411 | 113.1 | 113.5588 | 114.0176 | 114.4765 | 114.9353 | 115.3941 | 115.853 | 116.3118 | 116.7707 | 117.2295 | 117.6883 | 118.1472 | 118.606 | 119.0649 | 119.5237 | 119.9825 | 120.4414 | 120.9002 | 121.359 | 121.8179 | 122.2767 | 122.7356 | 123.1944 | 123.6532 | 124.1121 | 124.5709 | 125.0298 | 125.4886 | 125.9474 | 126.4063 | 126.8651 | 127.3239 | 127.7828 | 128.2416 | 128.7005 | 129.1593 | 129.6181 | 130.077 | 130.5358 | 130.9946 | 131.4535 | 131.9123 | 132.3712 | 132.83 | 133.2888 | 133.7477 | 134.2065 | 134.6654 | 135.1242 | 135.583 | 136.0419 | 136.5007 | 136.9595 | 137.4184 | 137.8772 | 138.3361 | 138.7949 | 139.2537 | 139.7126 | 140.1714 | 140.6303 | 141.0891 | 141.5479 | 142.0068 | 142.4656 | 142.9244 | 143.3833 | 143.8421 | 144.301 | 144.7598
|  | 150 | 79.5224 | 79.9813 | 80.4401 | 80.8989 | 81.3578 | 81.8166 | 82.2755 | 82.7343 | 83.1931 | 83.652 | 84.1108 | 84.5697 | 85.0285 | 85.4873 | 85.9462 | 86.405 | 86.8638 | 87.3227 | 87.7815 | 88.2404 | 88.6992 | 89.158 | 89.6169 | 90.0757 | 90.5346 | 90.9934 | 91.4522 | 91.9111 | 92.3699 | 92.8287 | 93.2876 | 93.7464 | 94.2053 | 94.6641 | 95.1229 | 95.5818 | 96.0406 | 96.4995 | 96.9583 | 97.4171 | 97.876 | 98.3348 | 98.7936 | 99.2525 | 99.7113 | 100.1702 | 100.629 | 101.0878 | 101.5467 | 102.0055 | 102.4643 | 102.9232 | 103.382 | 103.8409 | 104.2997 | 104.7585 | 105.2174 | 105.6762 | 106.1351 | 106.5939 | 107.0527 | 107.5116 | 107.9704 | 108.4292 | 108.8881 | 109.3469 | 109.8058 | 110.2646 | 110.7234 | 111.1823 | 111.6411 | 112.1 | 112.5588 | 113.0176 | 113.4765 | 113.9353 | 114.3941 | 114.853 | 115.3118 | 115.7707 | 116.2295 | 116.6883 | 117.1472 | 117.606 | 118.0649 | 118.5237 | 118.9825 | 119.4414 | 119.9002 | 120.359 | 120.8179 | 121.2767 | 121.7356 | 122.1944 | 122.6532 | 123.1121 | 123.5709 | 124.0298 | 124.4886 | 124.9474 | 125.4063 | 125.8651 | 126.3239 | 126.7828 | 127.2416 | 127.7005 | 128.1593 | 128.6181 | 129.077 | 129.5358 | 129.9946 | 130.4535 | 130.9123 | 131.3712 | 131.83 | 132.2888 | 132.7477 | 133.2065 | 133.6654 | 134.1242 | 134.583 | 135.0419 | 135.5007 | 135.9595 | 136.4184 | 136.8772 | 137.3361 | 137.7949 | 138.2537 | 138.7126 | 139.1714 | 139.6303 | 140.0891 | 140.5479 | 141.0068 | 141.4656 | 141.9244 | 142.3833 | 142.8421 | 143.301 | 143.7598
|  | 149 | 78.5224 | 78.9813 | 79.4401 | 79.8989 | 80.3578 | 80.8166 | 81.2755 | 81.7343 | 82.1931 | 82.652 | 83.1108 | 83.5697 | 84.0285 | 84.4873 | 84.9462 | 85.405 | 85.8638 | 86.3227 | 86.7815 | 87.2404 | 87.6992 | 88.158 | 88.6169 | 89.0757 | 89.5346 | 89.9934 | 90.4522 | 90.9111 | 91.3699 | 91.8287 | 92.2876 | 92.7464 | 93.2053 | 93.6641 | 94.1229 | 94.5818 | 95.0406 | 95.4995 | 95.9583 | 96.4171 | 96.876 | 97.3348 | 97.7936 | 98.2525 | 98.7113 | 99.1702 | 99.629 | 100.0878 | 100.5467 | 101.0055 | 101.4643 | 101.9232 | 102.382 | 102.8409 | 103.2997 | 103.7585 | 104.2174 | 104.6762 | 105.1351 | 105.5939 | 106.0527 | 106.5116 | 106.9704 | 107.4292 | 107.8881 | 108.3469 | 108.8058 | 109.2646 | 109.7234 | 110.1823 | 110.6411 | 111.1 | 111.5588 | 112.0176 | 112.4765 | 112.9353 | 113.3941 | 113.853 | 114.3118 | 114.7707 | 115.2295 | 115.6883 | 116.1472 | 116.606 | 117.0649 | 117.5237 | 117.9825 | 118.4414 | 118.9002 | 119.359 | 119.8179 | 120.2767 | 120.7356 | 121.1944 | 121.6532 | 122.1121 | 122.5709 | 123.0298 | 123.4886 | 123.9474 | 124.4063 | 124.8651 | 125.3239 | 125.7828 | 126.2416 | 126.7005 | 127.1593 | 127.6181 | 128.077 | 128.5358 | 128.9946 | 129.4535 | 129.9123 | 130.3712 | 130.83 | 131.2888 | 131.7477 | 132.2065 | 132.6654 | 133.1242 | 133.583 | 134.0419 | 134.5007 | 134.9595 | 135.4184 | 135.8772 | 136.3361 | 136.7949 | 137.2537 | 137.7126 | 138.1714 | 138.6303 | 139.0891 | 139.5479 | 140.0068 | 140.4656 | 140.9244 | 141.3833 | 141.8421 | 142.301 | 142.7598
|  | 148 | 77.5224 | 77.9813 | 78.4401 | 78.8989 | 79.3578 | 79.8166 | 80.2755 | 80.7343 | 81.1931 | 81.652 | 82.1108 | 82.5697 | 83.0285 | 83.4873 | 83.9462 | 84.405 | 84.8638 | 85.3227 | 85.7815 | 86.2404 | 86.6992 | 87.158 | 87.6169 | 88.0757 | 88.5346 | 88.9934 | 89.4522 | 89.9111 | 90.3699 | 90.8287 | 91.2876 | 91.7464 | 92.2053 | 92.6641 | 93.1229 | 93.5818 | 94.0406 | 94.4995 | 94.9583 | 95.4171 | 95.876 | 96.3348 | 96.7936 | 97.2525 | 97.7113 | 98.1702 | 98.629 | 99.0878 | 99.5467 | 100.0055 | 100.4643 | 100.9232 | 101.382 | 101.8409 | 102.2997 | 102.7585 | 103.2174 | 103.6762 | 104.1351 | 104.5939 | 105.0527 | 105.5116 | 105.9704 | 106.4292 | 106.8881 | 107.3469 | 107.8058 | 108.2646 | 108.7234 | 109.1823 | 109.6411 | 110.1 | 110.5588 | 111.0176 | 111.4765 | 111.9353 | 112.3941 | 112.853 | 113.3118 | 113.7707 | 114.2295 | 114.6883 | 115.1472 | 115.606 | 116.0649 | 116.5237 | 116.9825 | 117.4414 | 117.9002 | 118.359 | 118.8179 | 119.2767 | 119.7356 | 120.1944 | 120.6532 | 121.1121 | 121.5709 | 122.0298 | 122.4886 | 122.9474 | 123.4063 | 123.8651 | 124.3239 | 124.7828 | 125.2416 | 125.7005 | 126.1593 | 126.6181 | 127.077 | 127.5358 | 127.9946 | 128.4535 | 128.9123 | 129.3712 | 129.83 | 130.2888 | 130.7477 | 131.2065 | 131.6654 | 132.1242 | 132.583 | 133.0419 | 133.5007 | 133.9595 | 134.4184 | 134.8772 | 135.3361 | 135.7949 | 136.2537 | 136.7126 | 137.1714 | 137.6303 | 138.0891 | 138.5479 | 139.0068 | 139.4656 | 139.9244 | 140.3833 | 140.8421 | 141.301 | 141.7598
|  | 147 | 76.5224 | 76.9813 | 77.4401 | 77.8989 | 78.3578 | 78.8166 | 79.2755 | 79.7343 | 80.1931 | 80.652 | 81.1108 | 81.5697 | 82.0285 | 82.4873 | 82.9462 | 83.405 | 83.8638 | 84.3227 | 84.7815 | 85.2404 | 85.6992 | 86.158 | 86.6169 | 87.0757 | 87.5346 | 87.9934 | 88.4522 | 88.9111 | 89.3699 | 89.8287 | 90.2876 | 90.7464 | 91.2053 | 91.6641 | 92.1229 | 92.5818 | 93.0406 | 93.4995 | 93.9583 | 94.4171 | 94.876 | 95.3348 | 95.7936 | 96.2525 | 96.7113 | 97.1702 | 97.629 | 98.0878 | 98.5467 | 99.0055 | 99.4643 | 99.9232 | 100.382 | 100.8409 | 101.2997 | 101.7585 | 102.2174 | 102.6762 | 103.1351 | 103.5939 | 104.0527 | 104.5116 | 104.9704 | 105.4292 | 105.8881 | 106.3469 | 106.8058 | 107.2646 | 107.7234 | 108.1823 | 108.6411 | 109.1 | 109.5588 | 110.0176 | 110.4765 | 110.9353 | 111.3941 | 111.853 | 112.3118 | 112.7707 | 113.2295 | 113.6883 | 114.1472 | 114.606 | 115.0649 | 115.5237 | 115.9825 | 116.4414 | 116.9002 | 117.359 | 117.8179 | 118.2767 | 118.7356 | 119.1944 | 119.6532 | 120.1121 | 120.5709 | 121.0298 | 121.4886 | 121.9474 | 122.4063 | 122.8651 | 123.3239 | 123.7828 | 124.2416 | 124.7005 | 125.1593 | 125.6181 | 126.077 | 126.5358 | 126.9946 | 127.4535 | 127.9123 | 128.3712 | 128.83 | 129.2888 | 129.7477 | 130.2065 | 130.6654 | 131.1242 | 131.583 | 132.0419 | 132.5007 | 132.9595 | 133.4184 | 133.8772 | 134.3361 | 134.7949 | 135.2537 | 135.7126 | 136.1714 | 136.6303 | 137.0891 | 137.5479 | 138.0068 | 138.4656 | 138.9244 | 139.3833 | 139.8421 | 140.301 | 140.7598
|  | 146 | 75.5224 | 75.9813 | 76.4401 | 76.8989 | 77.3578 | 77.8166 | 78.2755 | 78.7343 | 79.1931 | 79.652 | 80.1108 | 80.5697 | 81.0285 | 81.4873 | 81.9462 | 82.405 | 82.8638 | 83.3227 | 83.7815 | 84.2404 | 84.6992 | 85.158 | 85.6169 | 86.0757 | 86.5346 | 86.9934 | 87.4522 | 87.9111 | 88.3699 | 88.8287 | 89.2876 | 89.7464 | 90.2053 | 90.6641 | 91.1229 | 91.5818 | 92.0406 | 92.4995 | 92.9583 | 93.4171 | 93.876 | 94.3348 | 94.7936 | 95.2525 | 95.7113 | 96.1702 | 96.629 | 97.0878 | 97.5467 | 98.0055 | 98.4643 | 98.9232 | 99.382 | 99.8409 | 100.2997 | 100.7585 | 101.2174 | 101.6762 | 102.1351 | 102.5939 | 103.0527 | 103.5116 | 103.9704 | 104.4292 | 104.8881 | 105.3469 | 105.8058 | 106.2646 | 106.7234 | 107.1823 | 107.6411 | 108.1 | 108.5588 | 109.0176 | 109.4765 | 109.9353 | 110.3941 | 110.853 | 111.3118 | 111.7707 | 112.2295 | 112.6883 | 113.1472 | 113.606 | 114.0649 | 114.5237 | 114.9825 | 115.4414 | 115.9002 | 116.359 | 116.8179 | 117.2767 | 117.7356 | 118.1944 | 118.6532 | 119.1121 | 119.5709 | 120.0298 | 120.4886 | 120.9474 | 121.4063 | 121.8651 | 122.3239 | 122.7828 | 123.2416 | 123.7005 | 124.1593 | 124.6181 | 125.077 | 125.5358 | 125.9946 | 126.4535 | 126.9123 | 127.3712 | 127.83 | 128.2888 | 128.7477 | 129.2065 | 129.6654 | 130.1242 | 130.583 | 131.0419 | 131.5007 | 131.9595 | 132.4184 | 132.8772 | 133.3361 | 133.7949 | 134.2537 | 134.7126 | 135.1714 | 135.6303 | 136.0891 | 136.5479 | 137.0068 | 137.4656 | 137.9244 | 138.3833 | 138.8421 | 139.301 | 139.7598
|  | 145 | 74.5224 | 74.9813 | 75.4401 | 75.8989 | 76.3578 | 76.8166 | 77.2755 | 77.7343 | 78.1931 | 78.652 | 79.1108 | 79.5697 | 80.0285 | 80.4873 | 80.9462 | 81.405 | 81.8638 | 82.3227 | 82.7815 | 83.2404 | 83.6992 | 84.158 | 84.6169 | 85.0757 | 85.5346 | 85.9934 | 86.4522 | 86.9111 | 87.3699 | 87.8287 | 88.2876 | 88.7464 | 89.2053 | 89.6641 | 90.1229 | 90.5818 | 91.0406 | 91.4995 | 91.9583 | 92.4171 | 92.876 | 93.3348 | 93.7936 | 94.2525 | 94.7113 | 95.1702 | 95.629 | 96.0878 | 96.5467 | 97.0055 | 97.4643 | 97.9232 | 98.382 | 98.8409 | 99.2997 | 99.7585 | 100.2174 | 100.6762 | 101.1351 | 101.5939 | 102.0527 | 102.5116 | 102.9704 | 103.4292 | 103.8881 | 104.3469 | 104.8058 | 105.2646 | 105.7234 | 106.1823 | 106.6411 | 107.1 | 107.5588 | 108.0176 | 108.4765 | 108.9353 | 109.3941 | 109.853 | 110.3118 | 110.7707 | 111.2295 | 111.6883 | 112.1472 | 112.606 | 113.0649 | 113.5237 | 113.9825 | 114.4414 | 114.9002 | 115.359 | 115.8179 | 116.2767 | 116.7356 | 117.1944 | 117.6532 | 118.1121 | 118.5709 | 119.0298 | 119.4886 | 119.9474 | 120.4063 | 120.8651 | 121.3239 | 121.7828 | 122.2416 | 122.7005 | 123.1593 | 123.6181 | 124.077 | 124.5358 | 124.9946 | 125.4535 | 125.9123 | 126.3712 | 126.83 | 127.2888 | 127.7477 | 128.2065 | 128.6654 | 129.1242 | 129.583 | 130.0419 | 130.5007 | 130.9595 | 131.4184 | 131.8772 | 132.3361 | 132.7949 | 133.2537 | 133.7126 | 134.1714 | 134.6303 | 135.0891 | 135.5479 | 136.0068 | 136.4656 | 136.9244 | 137.3833 | 137.8421 | 138.301 | 138.7598
|  | 144 | 73.5224 | 73.9813 | 74.4401 | 74.8989 | 75.3578 | 75.8166 | 76.2755 | 76.7343 | 77.1931 | 77.652 | 78.1108 | 78.5697 | 79.0285 | 79.4873 | 79.9462 | 80.405 | 80.8638 | 81.3227 | 81.7815 | 82.2404 | 82.6992 | 83.158 | 83.6169 | 84.0757 | 84.5346 | 84.9934 | 85.4522 | 85.9111 | 86.3699 | 86.8287 | 87.2876 | 87.7464 | 88.2053 | 88.6641 | 89.1229 | 89.5818 | 90.0406 | 90.4995 | 90.9583 | 91.4171 | 91.876 | 92.3348 | 92.7936 | 93.2525 | 93.7113 | 94.1702 | 94.629 | 95.0878 | 95.5467 | 96.0055 | 96.4643 | 96.9232 | 97.382 | 97.8409 | 98.2997 | 98.7585 | 99.2174 | 99.6762 | 100.1351 | 100.5939 | 101.0527 | 101.5116 | 101.9704 | 102.4292 | 102.8881 | 103.3469 | 103.8058 | 104.2646 | 104.7234 | 105.1823 | 105.6411 | 106.1 | 106.5588 | 107.0176 | 107.4765 | 107.9353 | 108.3941 | 108.853 | 109.3118 | 109.7707 | 110.2295 | 110.6883 | 111.1472 | 111.606 | 112.0649 | 112.5237 | 112.9825 | 113.4414 | 113.9002 | 114.359 | 114.8179 | 115.2767 | 115.7356 | 116.1944 | 116.6532 | 117.1121 | 117.5709 | 118.0298 | 118.4886 | 118.9474 | 119.4063 | 119.8651 | 120.3239 | 120.7828 | 121.2416 | 121.7005 | 122.1593 | 122.6181 | 123.077 | 123.5358 | 123.9946 | 124.4535 | 124.9123 | 125.3712 | 125.83 | 126.2888 | 126.7477 | 127.2065 | 127.6654 | 128.1242 | 128.583 | 129.0419 | 129.5007 | 129.9595 | 130.4184 | 130.8772 | 131.3361 | 131.7949 | 132.2537 | 132.7126 | 133.1714 | 133.6303 | 134.0891 | 134.5479 | 135.0068 | 135.4656 | 135.9244 | 136.3833 | 136.8421 | 137.301 | 137.7598
|  | 143 | 72.5224 | 72.9813 | 73.4401 | 73.8989 | 74.3578 | 74.8166 | 75.2755 | 75.7343 | 76.1931 | 76.652 | 77.1108 | 77.5697 | 78.0285 | 78.4873 | 78.9462 | 79.405 | 79.8638 | 80.3227 | 80.7815 | 81.2404 | 81.6992 | 82.158 | 82.6169 | 83.0757 | 83.5346 | 83.9934 | 84.4522 | 84.9111 | 85.3699 | 85.8287 | 86.2876 | 86.7464 | 87.2053 | 87.6641 | 88.1229 | 88.5818 | 89.0406 | 89.4995 | 89.9583 | 90.4171 | 90.876 | 91.3348 | 91.7936 | 92.2525 | 92.7113 | 93.1702 | 93.629 | 94.0878 | 94.5467 | 95.0055 | 95.4643 | 95.9232 | 96.382 | 96.8409 | 97.2997 | 97.7585 | 98.2174 | 98.6762 | 99.1351 | 99.5939 | 100.0527 | 100.5116 | 100.9704 | 101.4292 | 101.8881 | 102.3469 | 102.8058 | 103.2646 | 103.7234 | 104.1823 | 104.6411 | 105.1 | 105.5588 | 106.0176 | 106.4765 | 106.9353 | 107.3941 | 107.853 | 108.3118 | 108.7707 | 109.2295 | 109.6883 | 110.1472 | 110.606 | 111.0649 | 111.5237 | 111.9825 | 112.4414 | 112.9002 | 113.359 | 113.8179 | 114.2767 | 114.7356 | 115.1944 | 115.6532 | 116.1121 | 116.5709 | 117.0298 | 117.4886 | 117.9474 | 118.4063 | 118.8651 | 119.3239 | 119.7828 | 120.2416 | 120.7005 | 121.1593 | 121.6181 | 122.077 | 122.5358 | 122.9946 | 123.4535 | 123.9123 | 124.3712 | 124.83 | 125.2888 | 125.7477 | 126.2065 | 126.6654 | 127.1242 | 127.583 | 128.0419 | 128.5007 | 128.9595 | 129.4184 | 129.8772 | 130.3361 | 130.7949 | 131.2537 | 131.7126 | 132.1714 | 132.6303 | 133.0891 | 133.5479 | 134.0068 | 134.4656 | 134.9244 | 135.3833 | 135.8421 | 136.301 | 136.7598
|  | 142 | 71.5224 | 71.9813 | 72.4401 | 72.8989 | 73.3578 | 73.8166 | 74.2755 | 74.7343 | 75.1931 | 75.652 | 76.1108 | 76.5697 | 77.0285 | 77.4873 | 77.9462 | 78.405 | 78.8638 | 79.3227 | 79.7815 | 80.2404 | 80.6992 | 81.158 | 81.6169 | 82.0757 | 82.5346 | 82.9934 | 83.4522 | 83.9111 | 84.3699 | 84.8287 | 85.2876 | 85.7464 | 86.2053 | 86.6641 | 87.1229 | 87.5818 | 88.0406 | 88.4995 | 88.9583 | 89.4171 | 89.876 | 90.3348 | 90.7936 | 91.2525 | 91.7113 | 92.1702 | 92.629 | 93.0878 | 93.5467 | 94.0055 | 94.4643 | 94.9232 | 95.382 | 95.8409 | 96.2997 | 96.7585 | 97.2174 | 97.6762 | 98.1351 | 98.5939 | 99.0527 | 99.5116 | 99.9704 | 100.4292 | 100.8881 | 101.3469 | 101.8058 | 102.2646 | 102.7234 | 103.1823 | 103.6411 | 104.1 | 104.5588 | 105.0176 | 105.4765 | 105.9353 | 106.3941 | 106.853 | 107.3118 | 107.7707 | 108.2295 | 108.6883 | 109.1472 | 109.606 | 110.0649 | 110.5237 | 110.9825 | 111.4414 | 111.9002 | 112.359 | 112.8179 | 113.2767 | 113.7356 | 114.1944 | 114.6532 | 115.1121 | 115.5709 | 116.0298 | 116.4886 | 116.9474 | 117.4063 | 117.8651 | 118.3239 | 118.7828 | 119.2416 | 119.7005 | 120.1593 | 120.6181 | 121.077 | 121.5358 | 121.9946 | 122.4535 | 122.9123 | 123.3712 | 123.83 | 124.2888 | 124.7477 | 125.2065 | 125.6654 | 126.1242 | 126.583 | 127.0419 | 127.5007 | 127.9595 | 128.4184 | 128.8772 | 129.3361 | 129.7949 | 130.2537 | 130.7126 | 131.1714 | 131.6303 | 132.0891 | 132.5479 | 133.0068 | 133.4656 | 133.9244 | 134.3833 | 134.8421 | 135.301 | 135.7598
|  | 141 | 70.5224 | 70.9813 | 71.4401 | 71.8989 | 72.3578 | 72.8166 | 73.2755 | 73.7343 | 74.1931 | 74.652 | 75.1108 | 75.5697 | 76.0285 | 76.4873 | 76.9462 | 77.405 | 77.8638 | 78.3227 | 78.7815 | 79.2404 | 79.6992 | 80.158 | 80.6169 | 81.0757 | 81.5346 | 81.9934 | 82.4522 | 82.9111 | 83.3699 | 83.8287 | 84.2876 | 84.7464 | 85.2053 | 85.6641 | 86.1229 | 86.5818 | 87.0406 | 87.4995 | 87.9583 | 88.4171 | 88.876 | 89.3348 | 89.7936 | 90.2525 | 90.7113 | 91.1702 | 91.629 | 92.0878 | 92.5467 | 93.0055 | 93.4643 | 93.9232 | 94.382 | 94.8409 | 95.2997 | 95.7585 | 96.2174 | 96.6762 | 97.1351 | 97.5939 | 98.0527 | 98.5116 | 98.9704 | 99.4292 | 99.8881 | 100.3469 | 100.8058 | 101.2646 | 101.7234 | 102.1823 | 102.6411 | 103.1 | 103.5588 | 104.0176 | 104.4765 | 104.9353 | 105.3941 | 105.853 | 106.3118 | 106.7707 | 107.2295 | 107.6883 | 108.1472 | 108.606 | 109.0649 | 109.5237 | 109.9825 | 110.4414 | 110.9002 | 111.359 | 111.8179 | 112.2767 | 112.7356 | 113.1944 | 113.6532 | 114.1121 | 114.5709 | 115.0298 | 115.4886 | 115.9474 | 116.4063 | 116.8651 | 117.3239 | 117.7828 | 118.2416 | 118.7005 | 119.1593 | 119.6181 | 120.077 | 120.5358 | 120.9946 | 121.4535 | 121.9123 | 122.3712 | 122.83 | 123.2888 | 123.7477 | 124.2065 | 124.6654 | 125.1242 | 125.583 | 126.0419 | 126.5007 | 126.9595 | 127.4184 | 127.8772 | 128.3361 | 128.7949 | 129.2537 | 129.7126 | 130.1714 | 130.6303 | 131.0891 | 131.5479 | 132.0068 | 132.4656 | 132.9244 | 133.3833 | 133.8421 | 134.301 | 134.7598
|  | 140 | 69.5224 | 69.9813 | 70.4401 | 70.8989 | 71.3578 | 71.8166 | 72.2755 | 72.7343 | 73.1931 | 73.652 | 74.1108 | 74.5697 | 75.0285 | 75.4873 | 75.9462 | 76.405 | 76.8638 | 77.3227 | 77.7815 | 78.2404 | 78.6992 | 79.158 | 79.6169 | 80.0757 | 80.5346 | 80.9934 | 81.4522 | 81.9111 | 82.3699 | 82.8287 | 83.2876 | 83.7464 | 84.2053 | 84.6641 | 85.1229 | 85.5818 | 86.0406 | 86.4995 | 86.9583 | 87.4171 | 87.876 | 88.3348 | 88.7936 | 89.2525 | 89.7113 | 90.1702 | 90.629 | 91.0878 | 91.5467 | 92.0055 | 92.4643 | 92.9232 | 93.382 | 93.8409 | 94.2997 | 94.7585 | 95.2174 | 95.6762 | 96.1351 | 96.5939 | 97.0527 | 97.5116 | 97.9704 | 98.4292 | 98.8881 | 99.3469 | 99.8058 | 100.2646 | 100.7234 | 101.1823 | 101.6411 | 102.1 | 102.5588 | 103.0176 | 103.4765 | 103.9353 | 104.3941 | 104.853 | 105.3118 | 105.7707 | 106.2295 | 106.6883 | 107.1472 | 107.606 | 108.0649 | 108.5237 | 108.9825 | 109.4414 | 109.9002 | 110.359 | 110.8179 | 111.2767 | 111.7356 | 112.1944 | 112.6532 | 113.1121 | 113.5709 | 114.0298 | 114.4886 | 114.9474 | 115.4063 | 115.8651 | 116.3239 | 116.7828 | 117.2416 | 117.7005 | 118.1593 | 118.6181 | 119.077 | 119.5358 | 119.9946 | 120.4535 | 120.9123 | 121.3712 | 121.83 | 122.2888 | 122.7477 | 123.2065 | 123.6654 | 124.1242 | 124.583 | 125.0419 | 125.5007 | 125.9595 | 126.4184 | 126.8772 | 127.3361 | 127.7949 | 128.2537 | 128.7126 | 129.1714 | 129.6303 | 130.0891 | 130.5479 | 131.0068 | 131.4656 | 131.9244 | 132.3833 | 132.8421 | 133.301 | 133.7598
|  | 139 | 68.5224 | 68.9813 | 69.4401 | 69.8989 | 70.3578 | 70.8166 | 71.2755 | 71.7343 | 72.1931 | 72.652 | 73.1108 | 73.5697 | 74.0285 | 74.4873 | 74.9462 | 75.405 | 75.8638 | 76.3227 | 76.7815 | 77.2404 | 77.6992 | 78.158 | 78.6169 | 79.0757 | 79.5346 | 79.9934 | 80.4522 | 80.9111 | 81.3699 | 81.8287 | 82.2876 | 82.7464 | 83.2053 | 83.6641 | 84.1229 | 84.5818 | 85.0406 | 85.4995 | 85.9583 | 86.4171 | 86.876 | 87.3348 | 87.7936 | 88.2525 | 88.7113 | 89.1702 | 89.629 | 90.0878 | 90.5467 | 91.0055 | 91.4643 | 91.9232 | 92.382 | 92.8409 | 93.2997 | 93.7585 | 94.2174 | 94.6762 | 95.1351 | 95.5939 | 96.0527 | 96.5116 | 96.9704 | 97.4292 | 97.8881 | 98.3469 | 98.8058 | 99.2646 | 99.7234 | 100.1823 | 100.6411 | 101.1 | 101.5588 | 102.0176 | 102.4765 | 102.9353 | 103.3941 | 103.853 | 104.3118 | 104.7707 | 105.2295 | 105.6883 | 106.1472 | 106.606 | 107.0649 | 107.5237 | 107.9825 | 108.4414 | 108.9002 | 109.359 | 109.8179 | 110.2767 | 110.7356 | 111.1944 | 111.6532 | 112.1121 | 112.5709 | 113.0298 | 113.4886 | 113.9474 | 114.4063 | 114.8651 | 115.3239 | 115.7828 | 116.2416 | 116.7005 | 117.1593 | 117.6181 | 118.077 | 118.5358 | 118.9946 | 119.4535 | 119.9123 | 120.3712 | 120.83 | 121.2888 | 121.7477 | 122.2065 | 122.6654 | 123.1242 | 123.583 | 124.0419 | 124.5007 | 124.9595 | 125.4184 | 125.8772 | 126.3361 | 126.7949 | 127.2537 | 127.7126 | 128.1714 | 128.6303 | 129.0891 | 129.5479 | 130.0068 | 130.4656 | 130.9244 | 131.3833 | 131.8421 | 132.301 | 132.7598
|  | 138 | 67.5224 | 67.9813 | 68.4401 | 68.8989 | 69.3578 | 69.8166 | 70.2755 | 70.7343 | 71.1931 | 71.652 | 72.1108 | 72.5697 | 73.0285 | 73.4873 | 73.9462 | 74.405 | 74.8638 | 75.3227 | 75.7815 | 76.2404 | 76.6992 | 77.158 | 77.6169 | 78.0757 | 78.5346 | 78.9934 | 79.4522 | 79.9111 | 80.3699 | 80.8287 | 81.2876 | 81.7464 | 82.2053 | 82.6641 | 83.1229 | 83.5818 | 84.0406 | 84.4995 | 84.9583 | 85.4171 | 85.876 | 86.3348 | 86.7936 | 87.2525 | 87.7113 | 88.1702 | 88.629 | 89.0878 | 89.5467 | 90.0055 | 90.4643 | 90.9232 | 91.382 | 91.8409 | 92.2997 | 92.7585 | 93.2174 | 93.6762 | 94.1351 | 94.5939 | 95.0527 | 95.5116 | 95.9704 | 96.4292 | 96.8881 | 97.3469 | 97.8058 | 98.2646 | 98.7234 | 99.1823 | 99.6411 | 100.1 | 100.5588 | 101.0176 | 101.4765 | 101.9353 | 102.3941 | 102.853 | 103.3118 | 103.7707 | 104.2295 | 104.6883 | 105.1472 | 105.606 | 106.0649 | 106.5237 | 106.9825 | 107.4414 | 107.9002 | 108.359 | 108.8179 | 109.2767 | 109.7356 | 110.1944 | 110.6532 | 111.1121 | 111.5709 | 112.0298 | 112.4886 | 112.9474 | 113.4063 | 113.8651 | 114.3239 | 114.7828 | 115.2416 | 115.7005 | 116.1593 | 116.6181 | 117.077 | 117.5358 | 117.9946 | 118.4535 | 118.9123 | 119.3712 | 119.83 | 120.2888 | 120.7477 | 121.2065 | 121.6654 | 122.1242 | 122.583 | 123.0419 | 123.5007 | 123.9595 | 124.4184 | 124.8772 | 125.3361 | 125.7949 | 126.2537 | 126.7126 | 127.1714 | 127.6303 | 128.0891 | 128.5479 | 129.0068 | 129.4656 | 129.9244 | 130.3833 | 130.8421 | 131.301 | 131.7598
|  | 137 | 66.5224 | 66.9813 | 67.4401 | 67.8989 | 68.3578 | 68.8166 | 69.2755 | 69.7343 | 70.1931 | 70.652 | 71.1108 | 71.5697 | 72.0285 | 72.4873 | 72.9462 | 73.405 | 73.8638 | 74.3227 | 74.7815 | 75.2404 | 75.6992 | 76.158 | 76.6169 | 77.0757 | 77.5346 | 77.9934 | 78.4522 | 78.9111 | 79.3699 | 79.8287 | 80.2876 | 80.7464 | 81.2053 | 81.6641 | 82.1229 | 82.5818 | 83.0406 | 83.4995 | 83.9583 | 84.4171 | 84.876 | 85.3348 | 85.7936 | 86.2525 | 86.7113 | 87.1702 | 87.629 | 88.0878 | 88.5467 | 89.0055 | 89.4643 | 89.9232 | 90.382 | 90.8409 | 91.2997 | 91.7585 | 92.2174 | 92.6762 | 93.1351 | 93.5939 | 94.0527 | 94.5116 | 94.9704 | 95.4292 | 95.8881 | 96.3469 | 96.8058 | 97.2646 | 97.7234 | 98.1823 | 98.6411 | 99.1 | 99.5588 | 100.0176 | 100.4765 | 100.9353 | 101.3941 | 101.853 | 102.3118 | 102.7707 | 103.2295 | 103.6883 | 104.1472 | 104.606 | 105.0649 | 105.5237 | 105.9825 | 106.4414 | 106.9002 | 107.359 | 107.8179 | 108.2767 | 108.7356 | 109.1944 | 109.6532 | 110.1121 | 110.5709 | 111.0298 | 111.4886 | 111.9474 | 112.4063 | 112.8651 | 113.3239 | 113.7828 | 114.2416 | 114.7005 | 115.1593 | 115.6181 | 116.077 | 116.5358 | 116.9946 | 117.4535 | 117.9123 | 118.3712 | 118.83 | 119.2888 | 119.7477 | 120.2065 | 120.6654 | 121.1242 | 121.583 | 122.0419 | 122.5007 | 122.9595 | 123.4184 | 123.8772 | 124.3361 | 124.7949 | 125.2537 | 125.7126 | 126.1714 | 126.6303 | 127.0891 | 127.5479 | 128.0068 | 128.4656 | 128.9244 | 129.3833 | 129.8421 | 130.301 | 130.7598
|  | 136 | 65.5224 | 65.9813 | 66.4401 | 66.8989 | 67.3578 | 67.8166 | 68.2755 | 68.7343 | 69.1931 | 69.652 | 70.1108 | 70.5697 | 71.0285 | 71.4873 | 71.9462 | 72.405 | 72.8638 | 73.3227 | 73.7815 | 74.2404 | 74.6992 | 75.158 | 75.6169 | 76.0757 | 76.5346 | 76.9934 | 77.4522 | 77.9111 | 78.3699 | 78.8287 | 79.2876 | 79.7464 | 80.2053 | 80.6641 | 81.1229 | 81.5818 | 82.0406 | 82.4995 | 82.9583 | 83.4171 | 83.876 | 84.3348 | 84.7936 | 85.2525 | 85.7113 | 86.1702 | 86.629 | 87.0878 | 87.5467 | 88.0055 | 88.4643 | 88.9232 | 89.382 | 89.8409 | 90.2997 | 90.7585 | 91.2174 | 91.6762 | 92.1351 | 92.5939 | 93.0527 | 93.5116 | 93.9704 | 94.4292 | 94.8881 | 95.3469 | 95.8058 | 96.2646 | 96.7234 | 97.1823 | 97.6411 | 98.1 | 98.5588 | 99.0176 | 99.4765 | 99.9353 | 100.3941 | 100.853 | 101.3118 | 101.7707 | 102.2295 | 102.6883 | 103.1472 | 103.606 | 104.0649 | 104.5237 | 104.9825 | 105.4414 | 105.9002 | 106.359 | 106.8179 | 107.2767 | 107.7356 | 108.1944 | 108.6532 | 109.1121 | 109.5709 | 110.0298 | 110.4886 | 110.9474 | 111.4063 | 111.8651 | 112.3239 | 112.7828 | 113.2416 | 113.7005 | 114.1593 | 114.6181 | 115.077 | 115.5358 | 115.9946 | 116.4535 | 116.9123 | 117.3712 | 117.83 | 118.2888 | 118.7477 | 119.2065 | 119.6654 | 120.1242 | 120.583 | 121.0419 | 121.5007 | 121.9595 | 122.4184 | 122.8772 | 123.3361 | 123.7949 | 124.2537 | 124.7126 | 125.1714 | 125.6303 | 126.0891 | 126.5479 | 127.0068 | 127.4656 | 127.9244 | 128.3833 | 128.8421 | 129.301 | 129.7598
|  | 135 | 64.5224 | 64.9813 | 65.4401 | 65.8989 | 66.3578 | 66.8166 | 67.2755 | 67.7343 | 68.1931 | 68.652 | 69.1108 | 69.5697 | 70.0285 | 70.4873 | 70.9462 | 71.405 | 71.8638 | 72.3227 | 72.7815 | 73.2404 | 73.6992 | 74.158 | 74.6169 | 75.0757 | 75.5346 | 75.9934 | 76.4522 | 76.9111 | 77.3699 | 77.8287 | 78.2876 | 78.7464 | 79.2053 | 79.6641 | 80.1229 | 80.5818 | 81.0406 | 81.4995 | 81.9583 | 82.4171 | 82.876 | 83.3348 | 83.7936 | 84.2525 | 84.7113 | 85.1702 | 85.629 | 86.0878 | 86.5467 | 87.0055 | 87.4643 | 87.9232 | 88.382 | 88.8409 | 89.2997 | 89.7585 | 90.2174 | 90.6762 | 91.1351 | 91.5939 | 92.0527 | 92.5116 | 92.9704 | 93.4292 | 93.8881 | 94.3469 | 94.8058 | 95.2646 | 95.7234 | 96.1823 | 96.6411 | 97.1 | 97.5588 | 98.0176 | 98.4765 | 98.9353 | 99.3941 | 99.853 | 100.3118 | 100.7707 | 101.2295 | 101.6883 | 102.1472 | 102.606 | 103.0649 | 103.5237 | 103.9825 | 104.4414 | 104.9002 | 105.359 | 105.8179 | 106.2767 | 106.7356 | 107.1944 | 107.6532 | 108.1121 | 108.5709 | 109.0298 | 109.4886 | 109.9474 | 110.4063 | 110.8651 | 111.3239 | 111.7828 | 112.2416 | 112.7005 | 113.1593 | 113.6181 | 114.077 | 114.5358 | 114.9946 | 115.4535 | 115.9123 | 116.3712 | 116.83 | 117.2888 | 117.7477 | 118.2065 | 118.6654 | 119.1242 | 119.583 | 120.0419 | 120.5007 | 120.9595 | 121.4184 | 121.8772 | 122.3361 | 122.7949 | 123.2537 | 123.7126 | 124.1714 | 124.6303 | 125.0891 | 125.5479 | 126.0068 | 126.4656 | 126.9244 | 127.3833 | 127.8421 | 128.301 | 128.7598
|  | 134 | 63.5224 | 63.9813 | 64.4401 | 64.8989 | 65.3578 | 65.8166 | 66.2755 | 66.7343 | 67.1931 | 67.652 | 68.1108 | 68.5697 | 69.0285 | 69.4873 | 69.9462 | 70.405 | 70.8638 | 71.3227 | 71.7815 | 72.2404 | 72.6992 | 73.158 | 73.6169 | 74.0757 | 74.5346 | 74.9934 | 75.4522 | 75.9111 | 76.3699 | 76.8287 | 77.2876 | 77.7464 | 78.2053 | 78.6641 | 79.1229 | 79.5818 | 80.0406 | 80.4995 | 80.9583 | 81.4171 | 81.876 | 82.3348 | 82.7936 | 83.2525 | 83.7113 | 84.1702 | 84.629 | 85.0878 | 85.5467 | 86.0055 | 86.4643 | 86.9232 | 87.382 | 87.8409 | 88.2997 | 88.7585 | 89.2174 | 89.6762 | 90.1351 | 90.5939 | 91.0527 | 91.5116 | 91.9704 | 92.4292 | 92.8881 | 93.3469 | 93.8058 | 94.2646 | 94.7234 | 95.1823 | 95.6411 | 96.1 | 96.5588 | 97.0176 | 97.4765 | 97.9353 | 98.3941 | 98.853 | 99.3118 | 99.7707 | 100.2295 | 100.6883 | 101.1472 | 101.606 | 102.0649 | 102.5237 | 102.9825 | 103.4414 | 103.9002 | 104.359 | 104.8179 | 105.2767 | 105.7356 | 106.1944 | 106.6532 | 107.1121 | 107.5709 | 108.0298 | 108.4886 | 108.9474 | 109.4063 | 109.8651 | 110.3239 | 110.7828 | 111.2416 | 111.7005 | 112.1593 | 112.6181 | 113.077 | 113.5358 | 113.9946 | 114.4535 | 114.9123 | 115.3712 | 115.83 | 116.2888 | 116.7477 | 117.2065 | 117.6654 | 118.1242 | 118.583 | 119.0419 | 119.5007 | 119.9595 | 120.4184 | 120.8772 | 121.3361 | 121.7949 | 122.2537 | 122.7126 | 123.1714 | 123.6303 | 124.0891 | 124.5479 | 125.0068 | 125.4656 | 125.9244 | 126.3833 | 126.8421 | 127.301 | 127.7598
|  | 133 | 62.5224 | 62.9813 | 63.4401 | 63.8989 | 64.3578 | 64.8166 | 65.2755 | 65.7343 | 66.1931 | 66.652 | 67.1108 | 67.5697 | 68.0285 | 68.4873 | 68.9462 | 69.405 | 69.8638 | 70.3227 | 70.7815 | 71.2404 | 71.6992 | 72.158 | 72.6169 | 73.0757 | 73.5346 | 73.9934 | 74.4522 | 74.9111 | 75.3699 | 75.8287 | 76.2876 | 76.7464 | 77.2053 | 77.6641 | 78.1229 | 78.5818 | 79.0406 | 79.4995 | 79.9583 | 80.4171 | 80.876 | 81.3348 | 81.7936 | 82.2525 | 82.7113 | 83.1702 | 83.629 | 84.0878 | 84.5467 | 85.0055 | 85.4643 | 85.9232 | 86.382 | 86.8409 | 87.2997 | 87.7585 | 88.2174 | 88.6762 | 89.1351 | 89.5939 | 90.0527 | 90.5116 | 90.9704 | 91.4292 | 91.8881 | 92.3469 | 92.8058 | 93.2646 | 93.7234 | 94.1823 | 94.6411 | 95.1 | 95.5588 | 96.0176 | 96.4765 | 96.9353 | 97.3941 | 97.853 | 98.3118 | 98.7707 | 99.2295 | 99.6883 | 100.1472 | 100.606 | 101.0649 | 101.5237 | 101.9825 | 102.4414 | 102.9002 | 103.359 | 103.8179 | 104.2767 | 104.7356 | 105.1944 | 105.6532 | 106.1121 | 106.5709 | 107.0298 | 107.4886 | 107.9474 | 108.4063 | 108.8651 | 109.3239 | 109.7828 | 110.2416 | 110.7005 | 111.1593 | 111.6181 | 112.077 | 112.5358 | 112.9946 | 113.4535 | 113.9123 | 114.3712 | 114.83 | 115.2888 | 115.7477 | 116.2065 | 116.6654 | 117.1242 | 117.583 | 118.0419 | 118.5007 | 118.9595 | 119.4184 | 119.8772 | 120.3361 | 120.7949 | 121.2537 | 121.7126 | 122.1714 | 122.6303 | 123.0891 | 123.5479 | 124.0068 | 124.4656 | 124.9244 | 125.3833 | 125.8421 | 126.301 | 126.7598
|  | 132 | 61.5224 | 61.9813 | 62.4401 | 62.8989 | 63.3578 | 63.8166 | 64.2755 | 64.7343 | 65.1931 | 65.652 | 66.1108 | 66.5697 | 67.0285 | 67.4873 | 67.9462 | 68.405 | 68.8638 | 69.3227 | 69.7815 | 70.2404 | 70.6992 | 71.158 | 71.6169 | 72.0757 | 72.5346 | 72.9934 | 73.4522 | 73.9111 | 74.3699 | 74.8287 | 75.2876 | 75.7464 | 76.2053 | 76.6641 | 77.1229 | 77.5818 | 78.0406 | 78.4995 | 78.9583 | 79.4171 | 79.876 | 80.3348 | 80.7936 | 81.2525 | 81.7113 | 82.1702 | 82.629 | 83.0878 | 83.5467 | 84.0055 | 84.4643 | 84.9232 | 85.382 | 85.8409 | 86.2997 | 86.7585 | 87.2174 | 87.6762 | 88.1351 | 88.5939 | 89.0527 | 89.5116 | 89.9704 | 90.4292 | 90.8881 | 91.3469 | 91.8058 | 92.2646 | 92.7234 | 93.1823 | 93.6411 | 94.1 | 94.5588 | 95.0176 | 95.4765 | 95.9353 | 96.3941 | 96.853 | 97.3118 | 97.7707 | 98.2295 | 98.6883 | 99.1472 | 99.606 | 100.0649 | 100.5237 | 100.9825 | 101.4414 | 101.9002 | 102.359 | 102.8179 | 103.2767 | 103.7356 | 104.1944 | 104.6532 | 105.1121 | 105.5709 | 106.0298 | 106.4886 | 106.9474 | 107.4063 | 107.8651 | 108.3239 | 108.7828 | 109.2416 | 109.7005 | 110.1593 | 110.6181 | 111.077 | 111.5358 | 111.9946 | 112.4535 | 112.9123 | 113.3712 | 113.83 | 114.2888 | 114.7477 | 115.2065 | 115.6654 | 116.1242 | 116.583 | 117.0419 | 117.5007 | 117.9595 | 118.4184 | 118.8772 | 119.3361 | 119.7949 | 120.2537 | 120.7126 | 121.1714 | 121.6303 | 122.0891 | 122.5479 | 123.0068 | 123.4656 | 123.9244 | 124.3833 | 124.8421 | 125.301 | 125.7598
|  | 131 | 60.5224 | 60.9813 | 61.4401 | 61.8989 | 62.3578 | 62.8166 | 63.2755 | 63.7343 | 64.1931 | 64.652 | 65.1108 | 65.5697 | 66.0285 | 66.4873 | 66.9462 | 67.405 | 67.8638 | 68.3227 | 68.7815 | 69.2404 | 69.6992 | 70.158 | 70.6169 | 71.0757 | 71.5346 | 71.9934 | 72.4522 | 72.9111 | 73.3699 | 73.8287 | 74.2876 | 74.7464 | 75.2053 | 75.6641 | 76.1229 | 76.5818 | 77.0406 | 77.4995 | 77.9583 | 78.4171 | 78.876 | 79.3348 | 79.7936 | 80.2525 | 80.7113 | 81.1702 | 81.629 | 82.0878 | 82.5467 | 83.0055 | 83.4643 | 83.9232 | 84.382 | 84.8409 | 85.2997 | 85.7585 | 86.2174 | 86.6762 | 87.1351 | 87.5939 | 88.0527 | 88.5116 | 88.9704 | 89.4292 | 89.8881 | 90.3469 | 90.8058 | 91.2646 | 91.7234 | 92.1823 | 92.6411 | 93.1 | 93.5588 | 94.0176 | 94.4765 | 94.9353 | 95.3941 | 95.853 | 96.3118 | 96.7707 | 97.2295 | 97.6883 | 98.1472 | 98.606 | 99.0649 | 99.5237 | 99.9825 | 100.4414 | 100.9002 | 101.359 | 101.8179 | 102.2767 | 102.7356 | 103.1944 | 103.6532 | 104.1121 | 104.5709 | 105.0298 | 105.4886 | 105.9474 | 106.4063 | 106.8651 | 107.3239 | 107.7828 | 108.2416 | 108.7005 | 109.1593 | 109.6181 | 110.077 | 110.5358 | 110.9946 | 111.4535 | 111.9123 | 112.3712 | 112.83 | 113.2888 | 113.7477 | 114.2065 | 114.6654 | 115.1242 | 115.583 | 116.0419 | 116.5007 | 116.9595 | 117.4184 | 117.8772 | 118.3361 | 118.7949 | 119.2537 | 119.7126 | 120.1714 | 120.6303 | 121.0891 | 121.5479 | 122.0068 | 122.4656 | 122.9244 | 123.3833 | 123.8421 | 124.301 | 124.7598
|  | 130 | 59.5224 | 59.9813 | 60.4401 | 60.8989 | 61.3578 | 61.8166 | 62.2755 | 62.7343 | 63.1931 | 63.652 | 64.1108 | 64.5697 | 65.0285 | 65.4873 | 65.9462 | 66.405 | 66.8638 | 67.3227 | 67.7815 | 68.2404 | 68.6992 | 69.158 | 69.6169 | 70.0757 | 70.5346 | 70.9934 | 71.4522 | 71.9111 | 72.3699 | 72.8287 | 73.2876 | 73.7464 | 74.2053 | 74.6641 | 75.1229 | 75.5818 | 76.0406 | 76.4995 | 76.9583 | 77.4171 | 77.876 | 78.3348 | 78.7936 | 79.2525 | 79.7113 | 80.1702 | 80.629 | 81.0878 | 81.5467 | 82.0055 | 82.4643 | 82.9232 | 83.382 | 83.8409 | 84.2997 | 84.7585 | 85.2174 | 85.6762 | 86.1351 | 86.5939 | 87.0527 | 87.5116 | 87.9704 | 88.4292 | 88.8881 | 89.3469 | 89.8058 | 90.2646 | 90.7234 | 91.1823 | 91.6411 | 92.1 | 92.5588 | 93.0176 | 93.4765 | 93.9353 | 94.3941 | 94.853 | 95.3118 | 95.7707 | 96.2295 | 96.6883 | 97.1472 | 97.606 | 98.0649 | 98.5237 | 98.9825 | 99.4414 | 99.9002 | 100.359 | 100.8179 | 101.2767 | 101.7356 | 102.1944 | 102.6532 | 103.1121 | 103.5709 | 104.0298 | 104.4886 | 104.9474 | 105.4063 | 105.8651 | 106.3239 | 106.7828 | 107.2416 | 107.7005 | 108.1593 | 108.6181 | 109.077 | 109.5358 | 109.9946 | 110.4535 | 110.9123 | 111.3712 | 111.83 | 112.2888 | 112.7477 | 113.2065 | 113.6654 | 114.1242 | 114.583 | 115.0419 | 115.5007 | 115.9595 | 116.4184 | 116.8772 | 117.3361 | 117.7949 | 118.2537 | 118.7126 | 119.1714 | 119.6303 | 120.0891 | 120.5479 | 121.0068 | 121.4656 | 121.9244 | 122.3833 | 122.8421 | 123.301 | 123.7598
|  | 129 | 58.5224 | 58.9813 | 59.4401 | 59.8989 | 60.3578 | 60.8166 | 61.2755 | 61.7343 | 62.1931 | 62.652 | 63.1108 | 63.5697 | 64.0285 | 64.4873 | 64.9462 | 65.405 | 65.8638 | 66.3227 | 66.7815 | 67.2404 | 67.6992 | 68.158 | 68.6169 | 69.0757 | 69.5346 | 69.9934 | 70.4522 | 70.9111 | 71.3699 | 71.8287 | 72.2876 | 72.7464 | 73.2053 | 73.6641 | 74.1229 | 74.5818 | 75.0406 | 75.4995 | 75.9583 | 76.4171 | 76.876 | 77.3348 | 77.7936 | 78.2525 | 78.7113 | 79.1702 | 79.629 | 80.0878 | 80.5467 | 81.0055 | 81.4643 | 81.9232 | 82.382 | 82.8409 | 83.2997 | 83.7585 | 84.2174 | 84.6762 | 85.1351 | 85.5939 | 86.0527 | 86.5116 | 86.9704 | 87.4292 | 87.8881 | 88.3469 | 88.8058 | 89.2646 | 89.7234 | 90.1823 | 90.6411 | 91.1 | 91.5588 | 92.0176 | 92.4765 | 92.9353 | 93.3941 | 93.853 | 94.3118 | 94.7707 | 95.2295 | 95.6883 | 96.1472 | 96.606 | 97.0649 | 97.5237 | 97.9825 | 98.4414 | 98.9002 | 99.359 | 99.8179 | 100.2767 | 100.7356 | 101.1944 | 101.6532 | 102.1121 | 102.5709 | 103.0298 | 103.4886 | 103.9474 | 104.4063 | 104.8651 | 105.3239 | 105.7828 | 106.2416 | 106.7005 | 107.1593 | 107.6181 | 108.077 | 108.5358 | 108.9946 | 109.4535 | 109.9123 | 110.3712 | 110.83 | 111.2888 | 111.7477 | 112.2065 | 112.6654 | 113.1242 | 113.583 | 114.0419 | 114.5007 | 114.9595 | 115.4184 | 115.8772 | 116.3361 | 116.7949 | 117.2537 | 117.7126 | 118.1714 | 118.6303 | 119.0891 | 119.5479 | 120.0068 | 120.4656 | 120.9244 | 121.3833 | 121.8421 | 122.301 | 122.7598
|  | 128 | 57.5224 | 57.9813 | 58.4401 | 58.8989 | 59.3578 | 59.8166 | 60.2755 | 60.7343 | 61.1931 | 61.652 | 62.1108 | 62.5697 | 63.0285 | 63.4873 | 63.9462 | 64.405 | 64.8638 | 65.3227 | 65.7815 | 66.2404 | 66.6992 | 67.158 | 67.6169 | 68.0757 | 68.5346 | 68.9934 | 69.4522 | 69.9111 | 70.3699 | 70.8287 | 71.2876 | 71.7464 | 72.2053 | 72.6641 | 73.1229 | 73.5818 | 74.0406 | 74.4995 | 74.9583 | 75.4171 | 75.876 | 76.3348 | 76.7936 | 77.2525 | 77.7113 | 78.1702 | 78.629 | 79.0878 | 79.5467 | 80.0055 | 80.4643 | 80.9232 | 81.382 | 81.8409 | 82.2997 | 82.7585 | 83.2174 | 83.6762 | 84.1351 | 84.5939 | 85.0527 | 85.5116 | 85.9704 | 86.4292 | 86.8881 | 87.3469 | 87.8058 | 88.2646 | 88.7234 | 89.1823 | 89.6411 | 90.1 | 90.5588 | 91.0176 | 91.4765 | 91.9353 | 92.3941 | 92.853 | 93.3118 | 93.7707 | 94.2295 | 94.6883 | 95.1472 | 95.606 | 96.0649 | 96.5237 | 96.9825 | 97.4414 | 97.9002 | 98.359 | 98.8179 | 99.2767 | 99.7356 | 100.1944 | 100.6532 | 101.1121 | 101.5709 | 102.0298 | 102.4886 | 102.9474 | 103.4063 | 103.8651 | 104.3239 | 104.7828 | 105.2416 | 105.7005 | 106.1593 | 106.6181 | 107.077 | 107.5358 | 107.9946 | 108.4535 | 108.9123 | 109.3712 | 109.83 | 110.2888 | 110.7477 | 111.2065 | 111.6654 | 112.1242 | 112.583 | 113.0419 | 113.5007 | 113.9595 | 114.4184 | 114.8772 | 115.3361 | 115.7949 | 116.2537 | 116.7126 | 117.1714 | 117.6303 | 118.0891 | 118.5479 | 119.0068 | 119.4656 | 119.9244 | 120.3833 | 120.8421 | 121.301 | 121.7598
|  | 127 | 56.5224 | 56.9813 | 57.4401 | 57.8989 | 58.3578 | 58.8166 | 59.2755 | 59.7343 | 60.1931 | 60.652 | 61.1108 | 61.5697 | 62.0285 | 62.4873 | 62.9462 | 63.405 | 63.8638 | 64.3227 | 64.7815 | 65.2404 | 65.6992 | 66.158 | 66.6169 | 67.0757 | 67.5346 | 67.9934 | 68.4522 | 68.9111 | 69.3699 | 69.8287 | 70.2876 | 70.7464 | 71.2053 | 71.6641 | 72.1229 | 72.5818 | 73.0406 | 73.4995 | 73.9583 | 74.4171 | 74.876 | 75.3348 | 75.7936 | 76.2525 | 76.7113 | 77.1702 | 77.629 | 78.0878 | 78.5467 | 79.0055 | 79.4643 | 79.9232 | 80.382 | 80.8409 | 81.2997 | 81.7585 | 82.2174 | 82.6762 | 83.1351 | 83.5939 | 84.0527 | 84.5116 | 84.9704 | 85.4292 | 85.8881 | 86.3469 | 86.8058 | 87.2646 | 87.7234 | 88.1823 | 88.6411 | 89.1 | 89.5588 | 90.0176 | 90.4765 | 90.9353 | 91.3941 | 91.853 | 92.3118 | 92.7707 | 93.2295 | 93.6883 | 94.1472 | 94.606 | 95.0649 | 95.5237 | 95.9825 | 96.4414 | 96.9002 | 97.359 | 97.8179 | 98.2767 | 98.7356 | 99.1944 | 99.6532 | 100.1121 | 100.5709 | 101.0298 | 101.4886 | 101.9474 | 102.4063 | 102.8651 | 103.3239 | 103.7828 | 104.2416 | 104.7005 | 105.1593 | 105.6181 | 106.077 | 106.5358 | 106.9946 | 107.4535 | 107.9123 | 108.3712 | 108.83 | 109.2888 | 109.7477 | 110.2065 | 110.6654 | 111.1242 | 111.583 | 112.0419 | 112.5007 | 112.9595 | 113.4184 | 113.8772 | 114.3361 | 114.7949 | 115.2537 | 115.7126 | 116.1714 | 116.6303 | 117.0891 | 117.5479 | 118.0068 | 118.4656 | 118.9244 | 119.3833 | 119.8421 | 120.301 | 120.7598
|  | 126 | 55.5224 | 55.9813 | 56.4401 | 56.8989 | 57.3578 | 57.8166 | 58.2755 | 58.7343 | 59.1931 | 59.652 | 60.1108 | 60.5697 | 61.0285 | 61.4873 | 61.9462 | 62.405 | 62.8638 | 63.3227 | 63.7815 | 64.2404 | 64.6992 | 65.158 | 65.6169 | 66.0757 | 66.5346 | 66.9934 | 67.4522 | 67.9111 | 68.3699 | 68.8287 | 69.2876 | 69.7464 | 70.2053 | 70.6641 | 71.1229 | 71.5818 | 72.0406 | 72.4995 | 72.9583 | 73.4171 | 73.876 | 74.3348 | 74.7936 | 75.2525 | 75.7113 | 76.1702 | 76.629 | 77.0878 | 77.5467 | 78.0055 | 78.4643 | 78.9232 | 79.382 | 79.8409 | 80.2997 | 80.7585 | 81.2174 | 81.6762 | 82.1351 | 82.5939 | 83.0527 | 83.5116 | 83.9704 | 84.4292 | 84.8881 | 85.3469 | 85.8058 | 86.2646 | 86.7234 | 87.1823 | 87.6411 | 88.1 | 88.5588 | 89.0176 | 89.4765 | 89.9353 | 90.3941 | 90.853 | 91.3118 | 91.7707 | 92.2295 | 92.6883 | 93.1472 | 93.606 | 94.0649 | 94.5237 | 94.9825 | 95.4414 | 95.9002 | 96.359 | 96.8179 | 97.2767 | 97.7356 | 98.1944 | 98.6532 | 99.1121 | 99.5709 | 100.0298 | 100.4886 | 100.9474 | 101.4063 | 101.8651 | 102.3239 | 102.7828 | 103.2416 | 103.7005 | 104.1593 | 104.6181 | 105.077 | 105.5358 | 105.9946 | 106.4535 | 106.9123 | 107.3712 | 107.83 | 108.2888 | 108.7477 | 109.2065 | 109.6654 | 110.1242 | 110.583 | 111.0419 | 111.5007 | 111.9595 | 112.4184 | 112.8772 | 113.3361 | 113.7949 | 114.2537 | 114.7126 | 115.1714 | 115.6303 | 116.0891 | 116.5479 | 117.0068 | 117.4656 | 117.9244 | 118.3833 | 118.8421 | 119.301 | 119.7598
|  | 125 | 54.5224 | 54.9813 | 55.4401 | 55.8989 | 56.3578 | 56.8166 | 57.2755 | 57.7343 | 58.1931 | 58.652 | 59.1108 | 59.5697 | 60.0285 | 60.4873 | 60.9462 | 61.405 | 61.8638 | 62.3227 | 62.7815 | 63.2404 | 63.6992 | 64.158 | 64.6169 | 65.0757 | 65.5346 | 65.9934 | 66.4522 | 66.9111 | 67.3699 | 67.8287 | 68.2876 | 68.7464 | 69.2053 | 69.6641 | 70.1229 | 70.5818 | 71.0406 | 71.4995 | 71.9583 | 72.4171 | 72.876 | 73.3348 | 73.7936 | 74.2525 | 74.7113 | 75.1702 | 75.629 | 76.0878 | 76.5467 | 77.0055 | 77.4643 | 77.9232 | 78.382 | 78.8409 | 79.2997 | 79.7585 | 80.2174 | 80.6762 | 81.1351 | 81.5939 | 82.0527 | 82.5116 | 82.9704 | 83.4292 | 83.8881 | 84.3469 | 84.8058 | 85.2646 | 85.7234 | 86.1823 | 86.6411 | 87.1 | 87.5588 | 88.0176 | 88.4765 | 88.9353 | 89.3941 | 89.853 | 90.3118 | 90.7707 | 91.2295 | 91.6883 | 92.1472 | 92.606 | 93.0649 | 93.5237 | 93.9825 | 94.4414 | 94.9002 | 95.359 | 95.8179 | 96.2767 | 96.7356 | 97.1944 | 97.6532 | 98.1121 | 98.5709 | 99.0298 | 99.4886 | 99.9474 | 100.4063 | 100.8651 | 101.3239 | 101.7828 | 102.2416 | 102.7005 | 103.1593 | 103.6181 | 104.077 | 104.5358 | 104.9946 | 105.4535 | 105.9123 | 106.3712 | 106.83 | 107.2888 | 107.7477 | 108.2065 | 108.6654 | 109.1242 | 109.583 | 110.0419 | 110.5007 | 110.9595 | 111.4184 | 111.8772 | 112.3361 | 112.7949 | 113.2537 | 113.7126 | 114.1714 | 114.6303 | 115.0891 | 115.5479 | 116.0068 | 116.4656 | 116.9244 | 117.3833 | 117.8421 | 118.301 | 118.7598
|  | 124 | 53.5224 | 53.9813 | 54.4401 | 54.8989 | 55.3578 | 55.8166 | 56.2755 | 56.7343 | 57.1931 | 57.652 | 58.1108 | 58.5697 | 59.0285 | 59.4873 | 59.9462 | 60.405 | 60.8638 | 61.3227 | 61.7815 | 62.2404 | 62.6992 | 63.158 | 63.6169 | 64.0757 | 64.5346 | 64.9934 | 65.4522 | 65.9111 | 66.3699 | 66.8287 | 67.2876 | 67.7464 | 68.2053 | 68.6641 | 69.1229 | 69.5818 | 70.0406 | 70.4995 | 70.9583 | 71.4171 | 71.876 | 72.3348 | 72.7936 | 73.2525 | 73.7113 | 74.1702 | 74.629 | 75.0878 | 75.5467 | 76.0055 | 76.4643 | 76.9232 | 77.382 | 77.8409 | 78.2997 | 78.7585 | 79.2174 | 79.6762 | 80.1351 | 80.5939 | 81.0527 | 81.5116 | 81.9704 | 82.4292 | 82.8881 | 83.3469 | 83.8058 | 84.2646 | 84.7234 | 85.1823 | 85.6411 | 86.1 | 86.5588 | 87.0176 | 87.4765 | 87.9353 | 88.3941 | 88.853 | 89.3118 | 89.7707 | 90.2295 | 90.6883 | 91.1472 | 91.606 | 92.0649 | 92.5237 | 92.9825 | 93.4414 | 93.9002 | 94.359 | 94.8179 | 95.2767 | 95.7356 | 96.1944 | 96.6532 | 97.1121 | 97.5709 | 98.0298 | 98.4886 | 98.9474 | 99.4063 | 99.8651 | 100.3239 | 100.7828 | 101.2416 | 101.7005 | 102.1593 | 102.6181 | 103.077 | 103.5358 | 103.9946 | 104.4535 | 104.9123 | 105.3712 | 105.83 | 106.2888 | 106.7477 | 107.2065 | 107.6654 | 108.1242 | 108.583 | 109.0419 | 109.5007 | 109.9595 | 110.4184 | 110.8772 | 111.3361 | 111.7949 | 112.2537 | 112.7126 | 113.1714 | 113.6303 | 114.0891 | 114.5479 | 115.0068 | 115.4656 | 115.9244 | 116.3833 | 116.8421 | 117.301 | 117.7598
|  | 123 | 52.5224 | 52.9813 | 53.4401 | 53.8989 | 54.3578 | 54.8166 | 55.2755 | 55.7343 | 56.1931 | 56.652 | 57.1108 | 57.5697 | 58.0285 | 58.4873 | 58.9462 | 59.405 | 59.8638 | 60.3227 | 60.7815 | 61.2404 | 61.6992 | 62.158 | 62.6169 | 63.0757 | 63.5346 | 63.9934 | 64.4522 | 64.9111 | 65.3699 | 65.8287 | 66.2876 | 66.7464 | 67.2053 | 67.6641 | 68.1229 | 68.5818 | 69.0406 | 69.4995 | 69.9583 | 70.4171 | 70.876 | 71.3348 | 71.7936 | 72.2525 | 72.7113 | 73.1702 | 73.629 | 74.0878 | 74.5467 | 75.0055 | 75.4643 | 75.9232 | 76.382 | 76.8409 | 77.2997 | 77.7585 | 78.2174 | 78.6762 | 79.1351 | 79.5939 | 80.0527 | 80.5116 | 80.9704 | 81.4292 | 81.8881 | 82.3469 | 82.8058 | 83.2646 | 83.7234 | 84.1823 | 84.6411 | 85.1 | 85.5588 | 86.0176 | 86.4765 | 86.9353 | 87.3941 | 87.853 | 88.3118 | 88.7707 | 89.2295 | 89.6883 | 90.1472 | 90.606 | 91.0649 | 91.5237 | 91.9825 | 92.4414 | 92.9002 | 93.359 | 93.8179 | 94.2767 | 94.7356 | 95.1944 | 95.6532 | 96.1121 | 96.5709 | 97.0298 | 97.4886 | 97.9474 | 98.4063 | 98.8651 | 99.3239 | 99.7828 | 100.2416 | 100.7005 | 101.1593 | 101.6181 | 102.077 | 102.5358 | 102.9946 | 103.4535 | 103.9123 | 104.3712 | 104.83 | 105.2888 | 105.7477 | 106.2065 | 106.6654 | 107.1242 | 107.583 | 108.0419 | 108.5007 | 108.9595 | 109.4184 | 109.8772 | 110.3361 | 110.7949 | 111.2537 | 111.7126 | 112.1714 | 112.6303 | 113.0891 | 113.5479 | 114.0068 | 114.4656 | 114.9244 | 115.3833 | 115.8421 | 116.301 | 116.7598
|  | 122 | 51.5224 | 51.9813 | 52.4401 | 52.8989 | 53.3578 | 53.8166 | 54.2755 | 54.7343 | 55.1931 | 55.652 | 56.1108 | 56.5697 | 57.0285 | 57.4873 | 57.9462 | 58.405 | 58.8638 | 59.3227 | 59.7815 | 60.2404 | 60.6992 | 61.158 | 61.6169 | 62.0757 | 62.5346 | 62.9934 | 63.4522 | 63.9111 | 64.3699 | 64.8287 | 65.2876 | 65.7464 | 66.2053 | 66.6641 | 67.1229 | 67.5818 | 68.0406 | 68.4995 | 68.9583 | 69.4171 | 69.876 | 70.3348 | 70.7936 | 71.2525 | 71.7113 | 72.1702 | 72.629 | 73.0878 | 73.5467 | 74.0055 | 74.4643 | 74.9232 | 75.382 | 75.8409 | 76.2997 | 76.7585 | 77.2174 | 77.6762 | 78.1351 | 78.5939 | 79.0527 | 79.5116 | 79.9704 | 80.4292 | 80.8881 | 81.3469 | 81.8058 | 82.2646 | 82.7234 | 83.1823 | 83.6411 | 84.1 | 84.5588 | 85.0176 | 85.4765 | 85.9353 | 86.3941 | 86.853 | 87.3118 | 87.7707 | 88.2295 | 88.6883 | 89.1472 | 89.606 | 90.0649 | 90.5237 | 90.9825 | 91.4414 | 91.9002 | 92.359 | 92.8179 | 93.2767 | 93.7356 | 94.1944 | 94.6532 | 95.1121 | 95.5709 | 96.0298 | 96.4886 | 96.9474 | 97.4063 | 97.8651 | 98.3239 | 98.7828 | 99.2416 | 99.7005 | 100.1593 | 100.6181 | 101.077 | 101.5358 | 101.9946 | 102.4535 | 102.9123 | 103.3712 | 103.83 | 104.2888 | 104.7477 | 105.2065 | 105.6654 | 106.1242 | 106.583 | 107.0419 | 107.5007 | 107.9595 | 108.4184 | 108.8772 | 109.3361 | 109.7949 | 110.2537 | 110.7126 | 111.1714 | 111.6303 | 112.0891 | 112.5479 | 113.0068 | 113.4656 | 113.9244 | 114.3833 | 114.8421 | 115.301 | 115.7598
|  | 121 | 50.5224 | 50.9813 | 51.4401 | 51.8989 | 52.3578 | 52.8166 | 53.2755 | 53.7343 | 54.1931 | 54.652 | 55.1108 | 55.5697 | 56.0285 | 56.4873 | 56.9462 | 57.405 | 57.8638 | 58.3227 | 58.7815 | 59.2404 | 59.6992 | 60.158 | 60.6169 | 61.0757 | 61.5346 | 61.9934 | 62.4522 | 62.9111 | 63.3699 | 63.8287 | 64.2876 | 64.7464 | 65.2053 | 65.6641 | 66.1229 | 66.5818 | 67.0406 | 67.4995 | 67.9583 | 68.4171 | 68.876 | 69.3348 | 69.7936 | 70.2525 | 70.7113 | 71.1702 | 71.629 | 72.0878 | 72.5467 | 73.0055 | 73.4643 | 73.9232 | 74.382 | 74.8409 | 75.2997 | 75.7585 | 76.2174 | 76.6762 | 77.1351 | 77.5939 | 78.0527 | 78.5116 | 78.9704 | 79.4292 | 79.8881 | 80.3469 | 80.8058 | 81.2646 | 81.7234 | 82.1823 | 82.6411 | 83.1 | 83.5588 | 84.0176 | 84.4765 | 84.9353 | 85.3941 | 85.853 | 86.3118 | 86.7707 | 87.2295 | 87.6883 | 88.1472 | 88.606 | 89.0649 | 89.5237 | 89.9825 | 90.4414 | 90.9002 | 91.359 | 91.8179 | 92.2767 | 92.7356 | 93.1944 | 93.6532 | 94.1121 | 94.5709 | 95.0298 | 95.4886 | 95.9474 | 96.4063 | 96.8651 | 97.3239 | 97.7828 | 98.2416 | 98.7005 | 99.1593 | 99.6181 | 100.077 | 100.5358 | 100.9946 | 101.4535 | 101.9123 | 102.3712 | 102.83 | 103.2888 | 103.7477 | 104.2065 | 104.6654 | 105.1242 | 105.583 | 106.0419 | 106.5007 | 106.9595 | 107.4184 | 107.8772 | 108.3361 | 108.7949 | 109.2537 | 109.7126 | 110.1714 | 110.6303 | 111.0891 | 111.5479 | 112.0068 | 112.4656 | 112.9244 | 113.3833 | 113.8421 | 114.301 | 114.7598
|  | 120 | 49.5224 | 49.9813 | 50.4401 | 50.8989 | 51.3578 | 51.8166 | 52.2755 | 52.7343 | 53.1931 | 53.652 | 54.1108 | 54.5697 | 55.0285 | 55.4873 | 55.9462 | 56.405 | 56.8638 | 57.3227 | 57.7815 | 58.2404 | 58.6992 | 59.158 | 59.6169 | 60.0757 | 60.5346 | 60.9934 | 61.4522 | 61.9111 | 62.3699 | 62.8287 | 63.2876 | 63.7464 | 64.2053 | 64.6641 | 65.1229 | 65.5818 | 66.0406 | 66.4995 | 66.9583 | 67.4171 | 67.876 | 68.3348 | 68.7936 | 69.2525 | 69.7113 | 70.1702 | 70.629 | 71.0878 | 71.5467 | 72.0055 | 72.4643 | 72.9232 | 73.382 | 73.8409 | 74.2997 | 74.7585 | 75.2174 | 75.6762 | 76.1351 | 76.5939 | 77.0527 | 77.5116 | 77.9704 | 78.4292 | 78.8881 | 79.3469 | 79.8058 | 80.2646 | 80.7234 | 81.1823 | 81.6411 | 82.1 | 82.5588 | 83.0176 | 83.4765 | 83.9353 | 84.3941 | 84.853 | 85.3118 | 85.7707 | 86.2295 | 86.6883 | 87.1472 | 87.606 | 88.0649 | 88.5237 | 88.9825 | 89.4414 | 89.9002 | 90.359 | 90.8179 | 91.2767 | 91.7356 | 92.1944 | 92.6532 | 93.1121 | 93.5709 | 94.0298 | 94.4886 | 94.9474 | 95.4063 | 95.8651 | 96.3239 | 96.7828 | 97.2416 | 97.7005 | 98.1593 | 98.6181 | 99.077 | 99.5358 | 99.9946 | 100.4535 | 100.9123 | 101.3712 | 101.83 | 102.2888 | 102.7477 | 103.2065 | 103.6654 | 104.1242 | 104.583 | 105.0419 | 105.5007 | 105.9595 | 106.4184 | 106.8772 | 107.3361 | 107.7949 | 108.2537 | 108.7126 | 109.1714 | 109.6303 | 110.0891 | 110.5479 | 111.0068 | 111.4656 | 111.9244 | 112.3833 | 112.8421 | 113.301 | 113.7598
|  | 119 | 48.5224 | 48.9813 | 49.4401 | 49.8989 | 50.3578 | 50.8166 | 51.2755 | 51.7343 | 52.1931 | 52.652 | 53.1108 | 53.5697 | 54.0285 | 54.4873 | 54.9462 | 55.405 | 55.8638 | 56.3227 | 56.7815 | 57.2404 | 57.6992 | 58.158 | 58.6169 | 59.0757 | 59.5346 | 59.9934 | 60.4522 | 60.9111 | 61.3699 | 61.8287 | 62.2876 | 62.7464 | 63.2053 | 63.6641 | 64.1229 | 64.5818 | 65.0406 | 65.4995 | 65.9583 | 66.4171 | 66.876 | 67.3348 | 67.7936 | 68.2525 | 68.7113 | 69.1702 | 69.629 | 70.0878 | 70.5467 | 71.0055 | 71.4643 | 71.9232 | 72.382 | 72.8409 | 73.2997 | 73.7585 | 74.2174 | 74.6762 | 75.1351 | 75.5939 | 76.0527 | 76.5116 | 76.9704 | 77.4292 | 77.8881 | 78.3469 | 78.8058 | 79.2646 | 79.7234 | 80.1823 | 80.6411 | 81.1 | 81.5588 | 82.0176 | 82.4765 | 82.9353 | 83.3941 | 83.853 | 84.3118 | 84.7707 | 85.2295 | 85.6883 | 86.1472 | 86.606 | 87.0649 | 87.5237 | 87.9825 | 88.4414 | 88.9002 | 89.359 | 89.8179 | 90.2767 | 90.7356 | 91.1944 | 91.6532 | 92.1121 | 92.5709 | 93.0298 | 93.4886 | 93.9474 | 94.4063 | 94.8651 | 95.3239 | 95.7828 | 96.2416 | 96.7005 | 97.1593 | 97.6181 | 98.077 | 98.5358 | 98.9946 | 99.4535 | 99.9123 | 100.3712 | 100.83 | 101.2888 | 101.7477 | 102.2065 | 102.6654 | 103.1242 | 103.583 | 104.0419 | 104.5007 | 104.9595 | 105.4184 | 105.8772 | 106.3361 | 106.7949 | 107.2537 | 107.7126 | 108.1714 | 108.6303 | 109.0891 | 109.5479 | 110.0068 | 110.4656 | 110.9244 | 111.3833 | 111.8421 | 112.301 | 112.7598
|  | 118 | 47.5224 | 47.9813 | 48.4401 | 48.8989 | 49.3578 | 49.8166 | 50.2755 | 50.7343 | 51.1931 | 51.652 | 52.1108 | 52.5697 | 53.0285 | 53.4873 | 53.9462 | 54.405 | 54.8638 | 55.3227 | 55.7815 | 56.2404 | 56.6992 | 57.158 | 57.6169 | 58.0757 | 58.5346 | 58.9934 | 59.4522 | 59.9111 | 60.3699 | 60.8287 | 61.2876 | 61.7464 | 62.2053 | 62.6641 | 63.1229 | 63.5818 | 64.0406 | 64.4995 | 64.9583 | 65.4171 | 65.876 | 66.3348 | 66.7936 | 67.2525 | 67.7113 | 68.1702 | 68.629 | 69.0878 | 69.5467 | 70.0055 | 70.4643 | 70.9232 | 71.382 | 71.8409 | 72.2997 | 72.7585 | 73.2174 | 73.6762 | 74.1351 | 74.5939 | 75.0527 | 75.5116 | 75.9704 | 76.4292 | 76.8881 | 77.3469 | 77.8058 | 78.2646 | 78.7234 | 79.1823 | 79.6411 | 80.1 | 80.5588 | 81.0176 | 81.4765 | 81.9353 | 82.3941 | 82.853 | 83.3118 | 83.7707 | 84.2295 | 84.6883 | 85.1472 | 85.606 | 86.0649 | 86.5237 | 86.9825 | 87.4414 | 87.9002 | 88.359 | 88.8179 | 89.2767 | 89.7356 | 90.1944 | 90.6532 | 91.1121 | 91.5709 | 92.0298 | 92.4886 | 92.9474 | 93.4063 | 93.8651 | 94.3239 | 94.7828 | 95.2416 | 95.7005 | 96.1593 | 96.6181 | 97.077 | 97.5358 | 97.9946 | 98.4535 | 98.9123 | 99.3712 | 99.83 | 100.2888 | 100.7477 | 101.2065 | 101.6654 | 102.1242 | 102.583 | 103.0419 | 103.5007 | 103.9595 | 104.4184 | 104.8772 | 105.3361 | 105.7949 | 106.2537 | 106.7126 | 107.1714 | 107.6303 | 108.0891 | 108.5479 | 109.0068 | 109.4656 | 109.9244 | 110.3833 | 110.8421 | 111.301 | 111.7598
|  | 117 | 46.5224 | 46.9813 | 47.4401 | 47.8989 | 48.3578 | 48.8166 | 49.2755 | 49.7343 | 50.1931 | 50.652 | 51.1108 | 51.5697 | 52.0285 | 52.4873 | 52.9462 | 53.405 | 53.8638 | 54.3227 | 54.7815 | 55.2404 | 55.6992 | 56.158 | 56.6169 | 57.0757 | 57.5346 | 57.9934 | 58.4522 | 58.9111 | 59.3699 | 59.8287 | 60.2876 | 60.7464 | 61.2053 | 61.6641 | 62.1229 | 62.5818 | 63.0406 | 63.4995 | 63.9583 | 64.4171 | 64.876 | 65.3348 | 65.7936 | 66.2525 | 66.7113 | 67.1702 | 67.629 | 68.0878 | 68.5467 | 69.0055 | 69.4643 | 69.9232 | 70.382 | 70.8409 | 71.2997 | 71.7585 | 72.2174 | 72.6762 | 73.1351 | 73.5939 | 74.0527 | 74.5116 | 74.9704 | 75.4292 | 75.8881 | 76.3469 | 76.8058 | 77.2646 | 77.7234 | 78.1823 | 78.6411 | 79.1 | 79.5588 | 80.0176 | 80.4765 | 80.9353 | 81.3941 | 81.853 | 82.3118 | 82.7707 | 83.2295 | 83.6883 | 84.1472 | 84.606 | 85.0649 | 85.5237 | 85.9825 | 86.4414 | 86.9002 | 87.359 | 87.8179 | 88.2767 | 88.7356 | 89.1944 | 89.6532 | 90.1121 | 90.5709 | 91.0298 | 91.4886 | 91.9474 | 92.4063 | 92.8651 | 93.3239 | 93.7828 | 94.2416 | 94.7005 | 95.1593 | 95.6181 | 96.077 | 96.5358 | 96.9946 | 97.4535 | 97.9123 | 98.3712 | 98.83 | 99.2888 | 99.7477 | 100.2065 | 100.6654 | 101.1242 | 101.583 | 102.0419 | 102.5007 | 102.9595 | 103.4184 | 103.8772 | 104.3361 | 104.7949 | 105.2537 | 105.7126 | 106.1714 | 106.6303 | 107.0891 | 107.5479 | 108.0068 | 108.4656 | 108.9244 | 109.3833 | 109.8421 | 110.301 | 110.7598
|  | 116 | 45.5224 | 45.9813 | 46.4401 | 46.8989 | 47.3578 | 47.8166 | 48.2755 | 48.7343 | 49.1931 | 49.652 | 50.1108 | 50.5697 | 51.0285 | 51.4873 | 51.9462 | 52.405 | 52.8638 | 53.3227 | 53.7815 | 54.2404 | 54.6992 | 55.158 | 55.6169 | 56.0757 | 56.5346 | 56.9934 | 57.4522 | 57.9111 | 58.3699 | 58.8287 | 59.2876 | 59.7464 | 60.2053 | 60.6641 | 61.1229 | 61.5818 | 62.0406 | 62.4995 | 62.9583 | 63.4171 | 63.876 | 64.3348 | 64.7936 | 65.2525 | 65.7113 | 66.1702 | 66.629 | 67.0878 | 67.5467 | 68.0055 | 68.4643 | 68.9232 | 69.382 | 69.8409 | 70.2997 | 70.7585 | 71.2174 | 71.6762 | 72.1351 | 72.5939 | 73.0527 | 73.5116 | 73.9704 | 74.4292 | 74.8881 | 75.3469 | 75.8058 | 76.2646 | 76.7234 | 77.1823 | 77.6411 | 78.1 | 78.5588 | 79.0176 | 79.4765 | 79.9353 | 80.3941 | 80.853 | 81.3118 | 81.7707 | 82.2295 | 82.6883 | 83.1472 | 83.606 | 84.0649 | 84.5237 | 84.9825 | 85.4414 | 85.9002 | 86.359 | 86.8179 | 87.2767 | 87.7356 | 88.1944 | 88.6532 | 89.1121 | 89.5709 | 90.0298 | 90.4886 | 90.9474 | 91.4063 | 91.8651 | 92.3239 | 92.7828 | 93.2416 | 93.7005 | 94.1593 | 94.6181 | 95.077 | 95.5358 | 95.9946 | 96.4535 | 96.9123 | 97.3712 | 97.83 | 98.2888 | 98.7477 | 99.2065 | 99.6654 | 100.1242 | 100.583 | 101.0419 | 101.5007 | 101.9595 | 102.4184 | 102.8772 | 103.3361 | 103.7949 | 104.2537 | 104.7126 | 105.1714 | 105.6303 | 106.0891 | 106.5479 | 107.0068 | 107.4656 | 107.9244 | 108.3833 | 108.8421 | 109.301 | 109.7598
|  | 115 | 44.5224 | 44.9813 | 45.4401 | 45.8989 | 46.3578 | 46.8166 | 47.2755 | 47.7343 | 48.1931 | 48.652 | 49.1108 | 49.5697 | 50.0285 | 50.4873 | 50.9462 | 51.405 | 51.8638 | 52.3227 | 52.7815 | 53.2404 | 53.6992 | 54.158 | 54.6169 | 55.0757 | 55.5346 | 55.9934 | 56.4522 | 56.9111 | 57.3699 | 57.8287 | 58.2876 | 58.7464 | 59.2053 | 59.6641 | 60.1229 | 60.5818 | 61.0406 | 61.4995 | 61.9583 | 62.4171 | 62.876 | 63.3348 | 63.7936 | 64.2525 | 64.7113 | 65.1702 | 65.629 | 66.0878 | 66.5467 | 67.0055 | 67.4643 | 67.9232 | 68.382 | 68.8409 | 69.2997 | 69.7585 | 70.2174 | 70.6762 | 71.1351 | 71.5939 | 72.0527 | 72.5116 | 72.9704 | 73.4292 | 73.8881 | 74.3469 | 74.8058 | 75.2646 | 75.7234 | 76.1823 | 76.6411 | 77.1 | 77.5588 | 78.0176 | 78.4765 | 78.9353 | 79.3941 | 79.853 | 80.3118 | 80.7707 | 81.2295 | 81.6883 | 82.1472 | 82.606 | 83.0649 | 83.5237 | 83.9825 | 84.4414 | 84.9002 | 85.359 | 85.8179 | 86.2767 | 86.7356 | 87.1944 | 87.6532 | 88.1121 | 88.5709 | 89.0298 | 89.4886 | 89.9474 | 90.4063 | 90.8651 | 91.3239 | 91.7828 | 92.2416 | 92.7005 | 93.1593 | 93.6181 | 94.077 | 94.5358 | 94.9946 | 95.4535 | 95.9123 | 96.3712 | 96.83 | 97.2888 | 97.7477 | 98.2065 | 98.6654 | 99.1242 | 99.583 | 100.0419 | 100.5007 | 100.9595 | 101.4184 | 101.8772 | 102.3361 | 102.7949 | 103.2537 | 103.7126 | 104.1714 | 104.6303 | 105.0891 | 105.5479 | 106.0068 | 106.4656 | 106.9244 | 107.3833 | 107.8421 | 108.301 | 108.7598
|  | 114 | 43.5224 | 43.9813 | 44.4401 | 44.8989 | 45.3578 | 45.8166 | 46.2755 | 46.7343 | 47.1931 | 47.652 | 48.1108 | 48.5697 | 49.0285 | 49.4873 | 49.9462 | 50.405 | 50.8638 | 51.3227 | 51.7815 | 52.2404 | 52.6992 | 53.158 | 53.6169 | 54.0757 | 54.5346 | 54.9934 | 55.4522 | 55.9111 | 56.3699 | 56.8287 | 57.2876 | 57.7464 | 58.2053 | 58.6641 | 59.1229 | 59.5818 | 60.0406 | 60.4995 | 60.9583 | 61.4171 | 61.876 | 62.3348 | 62.7936 | 63.2525 | 63.7113 | 64.1702 | 64.629 | 65.0878 | 65.5467 | 66.0055 | 66.4643 | 66.9232 | 67.382 | 67.8409 | 68.2997 | 68.7585 | 69.2174 | 69.6762 | 70.1351 | 70.5939 | 71.0527 | 71.5116 | 71.9704 | 72.4292 | 72.8881 | 73.3469 | 73.8058 | 74.2646 | 74.7234 | 75.1823 | 75.6411 | 76.1 | 76.5588 | 77.0176 | 77.4765 | 77.9353 | 78.3941 | 78.853 | 79.3118 | 79.7707 | 80.2295 | 80.6883 | 81.1472 | 81.606 | 82.0649 | 82.5237 | 82.9825 | 83.4414 | 83.9002 | 84.359 | 84.8179 | 85.2767 | 85.7356 | 86.1944 | 86.6532 | 87.1121 | 87.5709 | 88.0298 | 88.4886 | 88.9474 | 89.4063 | 89.8651 | 90.3239 | 90.7828 | 91.2416 | 91.7005 | 92.1593 | 92.6181 | 93.077 | 93.5358 | 93.9946 | 94.4535 | 94.9123 | 95.3712 | 95.83 | 96.2888 | 96.7477 | 97.2065 | 97.6654 | 98.1242 | 98.583 | 99.0419 | 99.5007 | 99.9595 | 100.4184 | 100.8772 | 101.3361 | 101.7949 | 102.2537 | 102.7126 | 103.1714 | 103.6303 | 104.0891 | 104.5479 | 105.0068 | 105.4656 | 105.9244 | 106.3833 | 106.8421 | 107.301 | 107.7598
|  | 113 | 42.5224 | 42.9813 | 43.4401 | 43.8989 | 44.3578 | 44.8166 | 45.2755 | 45.7343 | 46.1931 | 46.652 | 47.1108 | 47.5697 | 48.0285 | 48.4873 | 48.9462 | 49.405 | 49.8638 | 50.3227 | 50.7815 | 51.2404 | 51.6992 | 52.158 | 52.6169 | 53.0757 | 53.5346 | 53.9934 | 54.4522 | 54.9111 | 55.3699 | 55.8287 | 56.2876 | 56.7464 | 57.2053 | 57.6641 | 58.1229 | 58.5818 | 59.0406 | 59.4995 | 59.9583 | 60.4171 | 60.876 | 61.3348 | 61.7936 | 62.2525 | 62.7113 | 63.1702 | 63.629 | 64.0878 | 64.5467 | 65.0055 | 65.4643 | 65.9232 | 66.382 | 66.8409 | 67.2997 | 67.7585 | 68.2174 | 68.6762 | 69.1351 | 69.5939 | 70.0527 | 70.5116 | 70.9704 | 71.4292 | 71.8881 | 72.3469 | 72.8058 | 73.2646 | 73.7234 | 74.1823 | 74.6411 | 75.1 | 75.5588 | 76.0176 | 76.4765 | 76.9353 | 77.3941 | 77.853 | 78.3118 | 78.7707 | 79.2295 | 79.6883 | 80.1472 | 80.606 | 81.0649 | 81.5237 | 81.9825 | 82.4414 | 82.9002 | 83.359 | 83.8179 | 84.2767 | 84.7356 | 85.1944 | 85.6532 | 86.1121 | 86.5709 | 87.0298 | 87.4886 | 87.9474 | 88.4063 | 88.8651 | 89.3239 | 89.7828 | 90.2416 | 90.7005 | 91.1593 | 91.6181 | 92.077 | 92.5358 | 92.9946 | 93.4535 | 93.9123 | 94.3712 | 94.83 | 95.2888 | 95.7477 | 96.2065 | 96.6654 | 97.1242 | 97.583 | 98.0419 | 98.5007 | 98.9595 | 99.4184 | 99.8772 | 100.3361 | 100.7949 | 101.2537 | 101.7126 | 102.1714 | 102.6303 | 103.0891 | 103.5479 | 104.0068 | 104.4656 | 104.9244 | 105.3833 | 105.8421 | 106.301 | 106.7598
|  | 112 | 41.5224 | 41.9813 | 42.4401 | 42.8989 | 43.3578 | 43.8166 | 44.2755 | 44.7343 | 45.1931 | 45.652 | 46.1108 | 46.5697 | 47.0285 | 47.4873 | 47.9462 | 48.405 | 48.8638 | 49.3227 | 49.7815 | 50.2404 | 50.6992 | 51.158 | 51.6169 | 52.0757 | 52.5346 | 52.9934 | 53.4522 | 53.9111 | 54.3699 | 54.8287 | 55.2876 | 55.7464 | 56.2053 | 56.6641 | 57.1229 | 57.5818 | 58.0406 | 58.4995 | 58.9583 | 59.4171 | 59.876 | 60.3348 | 60.7936 | 61.2525 | 61.7113 | 62.1702 | 62.629 | 63.0878 | 63.5467 | 64.0055 | 64.4643 | 64.9232 | 65.382 | 65.8409 | 66.2997 | 66.7585 | 67.2174 | 67.6762 | 68.1351 | 68.5939 | 69.0527 | 69.5116 | 69.9704 | 70.4292 | 70.8881 | 71.3469 | 71.8058 | 72.2646 | 72.7234 | 73.1823 | 73.6411 | 74.1 | 74.5588 | 75.0176 | 75.4765 | 75.9353 | 76.3941 | 76.853 | 77.3118 | 77.7707 | 78.2295 | 78.6883 | 79.1472 | 79.606 | 80.0649 | 80.5237 | 80.9825 | 81.4414 | 81.9002 | 82.359 | 82.8179 | 83.2767 | 83.7356 | 84.1944 | 84.6532 | 85.1121 | 85.5709 | 86.0298 | 86.4886 | 86.9474 | 87.4063 | 87.8651 | 88.3239 | 88.7828 | 89.2416 | 89.7005 | 90.1593 | 90.6181 | 91.077 | 91.5358 | 91.9946 | 92.4535 | 92.9123 | 93.3712 | 93.83 | 94.2888 | 94.7477 | 95.2065 | 95.6654 | 96.1242 | 96.583 | 97.0419 | 97.5007 | 97.9595 | 98.4184 | 98.8772 | 99.3361 | 99.7949 | 100.2537 | 100.7126 | 101.1714 | 101.6303 | 102.0891 | 102.5479 | 103.0068 | 103.4656 | 103.9244 | 104.3833 | 104.8421 | 105.301 | 105.7598
|  | 111 | 40.5224 | 40.9813 | 41.4401 | 41.8989 | 42.3578 | 42.8166 | 43.2755 | 43.7343 | 44.1931 | 44.652 | 45.1108 | 45.5697 | 46.0285 | 46.4873 | 46.9462 | 47.405 | 47.8638 | 48.3227 | 48.7815 | 49.2404 | 49.6992 | 50.158 | 50.6169 | 51.0757 | 51.5346 | 51.9934 | 52.4522 | 52.9111 | 53.3699 | 53.8287 | 54.2876 | 54.7464 | 55.2053 | 55.6641 | 56.1229 | 56.5818 | 57.0406 | 57.4995 | 57.9583 | 58.4171 | 58.876 | 59.3348 | 59.7936 | 60.2525 | 60.7113 | 61.1702 | 61.629 | 62.0878 | 62.5467 | 63.0055 | 63.4643 | 63.9232 | 64.382 | 64.8409 | 65.2997 | 65.7585 | 66.2174 | 66.6762 | 67.1351 | 67.5939 | 68.0527 | 68.5116 | 68.9704 | 69.4292 | 69.8881 | 70.3469 | 70.8058 | 71.2646 | 71.7234 | 72.1823 | 72.6411 | 73.1 | 73.5588 | 74.0176 | 74.4765 | 74.9353 | 75.3941 | 75.853 | 76.3118 | 76.7707 | 77.2295 | 77.6883 | 78.1472 | 78.606 | 79.0649 | 79.5237 | 79.9825 | 80.4414 | 80.9002 | 81.359 | 81.8179 | 82.2767 | 82.7356 | 83.1944 | 83.6532 | 84.1121 | 84.5709 | 85.0298 | 85.4886 | 85.9474 | 86.4063 | 86.8651 | 87.3239 | 87.7828 | 88.2416 | 88.7005 | 89.1593 | 89.6181 | 90.077 | 90.5358 | 90.9946 | 91.4535 | 91.9123 | 92.3712 | 92.83 | 93.2888 | 93.7477 | 94.2065 | 94.6654 | 95.1242 | 95.583 | 96.0419 | 96.5007 | 96.9595 | 97.4184 | 97.8772 | 98.3361 | 98.7949 | 99.2537 | 99.7126 | 100.1714 | 100.6303 | 101.0891 | 101.5479 | 102.0068 | 102.4656 | 102.9244 | 103.3833 | 103.8421 | 104.301 | 104.7598
|  | 110 | 39.5224 | 39.9813 | 40.4401 | 40.8989 | 41.3578 | 41.8166 | 42.2755 | 42.7343 | 43.1931 | 43.652 | 44.1108 | 44.5697 | 45.0285 | 45.4873 | 45.9462 | 46.405 | 46.8638 | 47.3227 | 47.7815 | 48.2404 | 48.6992 | 49.158 | 49.6169 | 50.0757 | 50.5346 | 50.9934 | 51.4522 | 51.9111 | 52.3699 | 52.8287 | 53.2876 | 53.7464 | 54.2053 | 54.6641 | 55.1229 | 55.5818 | 56.0406 | 56.4995 | 56.9583 | 57.4171 | 57.876 | 58.3348 | 58.7936 | 59.2525 | 59.7113 | 60.1702 | 60.629 | 61.0878 | 61.5467 | 62.0055 | 62.4643 | 62.9232 | 63.382 | 63.8409 | 64.2997 | 64.7585 | 65.2174 | 65.6762 | 66.1351 | 66.5939 | 67.0527 | 67.5116 | 67.9704 | 68.4292 | 68.8881 | 69.3469 | 69.8058 | 70.2646 | 70.7234 | 71.1823 | 71.6411 | 72.1 | 72.5588 | 73.0176 | 73.4765 | 73.9353 | 74.3941 | 74.853 | 75.3118 | 75.7707 | 76.2295 | 76.6883 | 77.1472 | 77.606 | 78.0649 | 78.5237 | 78.9825 | 79.4414 | 79.9002 | 80.359 | 80.8179 | 81.2767 | 81.7356 | 82.1944 | 82.6532 | 83.1121 | 83.5709 | 84.0298 | 84.4886 | 84.9474 | 85.4063 | 85.8651 | 86.3239 | 86.7828 | 87.2416 | 87.7005 | 88.1593 | 88.6181 | 89.077 | 89.5358 | 89.9946 | 90.4535 | 90.9123 | 91.3712 | 91.83 | 92.2888 | 92.7477 | 93.2065 | 93.6654 | 94.1242 | 94.583 | 95.0419 | 95.5007 | 95.9595 | 96.4184 | 96.8772 | 97.3361 | 97.7949 | 98.2537 | 98.7126 | 99.1714 | 99.6303 | 100.0891 | 100.5479 | 101.0068 | 101.4656 | 101.9244 | 102.3833 | 102.8421 | 103.301 | 103.7598
|  | 109 | 38.5224 | 38.9813 | 39.4401 | 39.8989 | 40.3578 | 40.8166 | 41.2755 | 41.7343 | 42.1931 | 42.652 | 43.1108 | 43.5697 | 44.0285 | 44.4873 | 44.9462 | 45.405 | 45.8638 | 46.3227 | 46.7815 | 47.2404 | 47.6992 | 48.158 | 48.6169 | 49.0757 | 49.5346 | 49.9934 | 50.4522 | 50.9111 | 51.3699 | 51.8287 | 52.2876 | 52.7464 | 53.2053 | 53.6641 | 54.1229 | 54.5818 | 55.0406 | 55.4995 | 55.9583 | 56.4171 | 56.876 | 57.3348 | 57.7936 | 58.2525 | 58.7113 | 59.1702 | 59.629 | 60.0878 | 60.5467 | 61.0055 | 61.4643 | 61.9232 | 62.382 | 62.8409 | 63.2997 | 63.7585 | 64.2174 | 64.6762 | 65.1351 | 65.5939 | 66.0527 | 66.5116 | 66.9704 | 67.4292 | 67.8881 | 68.3469 | 68.8058 | 69.2646 | 69.7234 | 70.1823 | 70.6411 | 71.1 | 71.5588 | 72.0176 | 72.4765 | 72.9353 | 73.3941 | 73.853 | 74.3118 | 74.7707 | 75.2295 | 75.6883 | 76.1472 | 76.606 | 77.0649 | 77.5237 | 77.9825 | 78.4414 | 78.9002 | 79.359 | 79.8179 | 80.2767 | 80.7356 | 81.1944 | 81.6532 | 82.1121 | 82.5709 | 83.0298 | 83.4886 | 83.9474 | 84.4063 | 84.8651 | 85.3239 | 85.7828 | 86.2416 | 86.7005 | 87.1593 | 87.6181 | 88.077 | 88.5358 | 88.9946 | 89.4535 | 89.9123 | 90.3712 | 90.83 | 91.2888 | 91.7477 | 92.2065 | 92.6654 | 93.1242 | 93.583 | 94.0419 | 94.5007 | 94.9595 | 95.4184 | 95.8772 | 96.3361 | 96.7949 | 97.2537 | 97.7126 | 98.1714 | 98.6303 | 99.0891 | 99.5479 | 100.0068 | 100.4656 | 100.9244 | 101.3833 | 101.8421 | 102.301 | 102.7598
|  | 108 | 37.5224 | 37.9813 | 38.4401 | 38.8989 | 39.3578 | 39.8166 | 40.2755 | 40.7343 | 41.1931 | 41.652 | 42.1108 | 42.5697 | 43.0285 | 43.4873 | 43.9462 | 44.405 | 44.8638 | 45.3227 | 45.7815 | 46.2404 | 46.6992 | 47.158 | 47.6169 | 48.0757 | 48.5346 | 48.9934 | 49.4522 | 49.9111 | 50.3699 | 50.8287 | 51.2876 | 51.7464 | 52.2053 | 52.6641 | 53.1229 | 53.5818 | 54.0406 | 54.4995 | 54.9583 | 55.4171 | 55.876 | 56.3348 | 56.7936 | 57.2525 | 57.7113 | 58.1702 | 58.629 | 59.0878 | 59.5467 | 60.0055 | 60.4643 | 60.9232 | 61.382 | 61.8409 | 62.2997 | 62.7585 | 63.2174 | 63.6762 | 64.1351 | 64.5939 | 65.0527 | 65.5116 | 65.9704 | 66.4292 | 66.8881 | 67.3469 | 67.8058 | 68.2646 | 68.7234 | 69.1823 | 69.6411 | 70.1 | 70.5588 | 71.0176 | 71.4765 | 71.9353 | 72.3941 | 72.853 | 73.3118 | 73.7707 | 74.2295 | 74.6883 | 75.1472 | 75.606 | 76.0649 | 76.5237 | 76.9825 | 77.4414 | 77.9002 | 78.359 | 78.8179 | 79.2767 | 79.7356 | 80.1944 | 80.6532 | 81.1121 | 81.5709 | 82.0298 | 82.4886 | 82.9474 | 83.4063 | 83.8651 | 84.3239 | 84.7828 | 85.2416 | 85.7005 | 86.1593 | 86.6181 | 87.077 | 87.5358 | 87.9946 | 88.4535 | 88.9123 | 89.3712 | 89.83 | 90.2888 | 90.7477 | 91.2065 | 91.6654 | 92.1242 | 92.583 | 93.0419 | 93.5007 | 93.9595 | 94.4184 | 94.8772 | 95.3361 | 95.7949 | 96.2537 | 96.7126 | 97.1714 | 97.6303 | 98.0891 | 98.5479 | 99.0068 | 99.4656 | 99.9244 | 100.3833 | 100.8421 | 101.301 | 101.7598
|  | 107 | 36.5224 | 36.9813 | 37.4401 | 37.8989 | 38.3578 | 38.8166 | 39.2755 | 39.7343 | 40.1931 | 40.652 | 41.1108 | 41.5697 | 42.0285 | 42.4873 | 42.9462 | 43.405 | 43.8638 | 44.3227 | 44.7815 | 45.2404 | 45.6992 | 46.158 | 46.6169 | 47.0757 | 47.5346 | 47.9934 | 48.4522 | 48.9111 | 49.3699 | 49.8287 | 50.2876 | 50.7464 | 51.2053 | 51.6641 | 52.1229 | 52.5818 | 53.0406 | 53.4995 | 53.9583 | 54.4171 | 54.876 | 55.3348 | 55.7936 | 56.2525 | 56.7113 | 57.1702 | 57.629 | 58.0878 | 58.5467 | 59.0055 | 59.4643 | 59.9232 | 60.382 | 60.8409 | 61.2997 | 61.7585 | 62.2174 | 62.6762 | 63.1351 | 63.5939 | 64.0527 | 64.5116 | 64.9704 | 65.4292 | 65.8881 | 66.3469 | 66.8058 | 67.2646 | 67.7234 | 68.1823 | 68.6411 | 69.1 | 69.5588 | 70.0176 | 70.4765 | 70.9353 | 71.3941 | 71.853 | 72.3118 | 72.7707 | 73.2295 | 73.6883 | 74.1472 | 74.606 | 75.0649 | 75.5237 | 75.9825 | 76.4414 | 76.9002 | 77.359 | 77.8179 | 78.2767 | 78.7356 | 79.1944 | 79.6532 | 80.1121 | 80.5709 | 81.0298 | 81.4886 | 81.9474 | 82.4063 | 82.8651 | 83.3239 | 83.7828 | 84.2416 | 84.7005 | 85.1593 | 85.6181 | 86.077 | 86.5358 | 86.9946 | 87.4535 | 87.9123 | 88.3712 | 88.83 | 89.2888 | 89.7477 | 90.2065 | 90.6654 | 91.1242 | 91.583 | 92.0419 | 92.5007 | 92.9595 | 93.4184 | 93.8772 | 94.3361 | 94.7949 | 95.2537 | 95.7126 | 96.1714 | 96.6303 | 97.0891 | 97.5479 | 98.0068 | 98.4656 | 98.9244 | 99.3833 | 99.8421 | 100.301 | 100.7598
|  | 106 | 35.5224 | 35.9813 | 36.4401 | 36.8989 | 37.3578 | 37.8166 | 38.2755 | 38.7343 | 39.1931 | 39.652 | 40.1108 | 40.5697 | 41.0285 | 41.4873 | 41.9462 | 42.405 | 42.8638 | 43.3227 | 43.7815 | 44.2404 | 44.6992 | 45.158 | 45.6169 | 46.0757 | 46.5346 | 46.9934 | 47.4522 | 47.9111 | 48.3699 | 48.8287 | 49.2876 | 49.7464 | 50.2053 | 50.6641 | 51.1229 | 51.5818 | 52.0406 | 52.4995 | 52.9583 | 53.4171 | 53.876 | 54.3348 | 54.7936 | 55.2525 | 55.7113 | 56.1702 | 56.629 | 57.0878 | 57.5467 | 58.0055 | 58.4643 | 58.9232 | 59.382 | 59.8409 | 60.2997 | 60.7585 | 61.2174 | 61.6762 | 62.1351 | 62.5939 | 63.0527 | 63.5116 | 63.9704 | 64.4292 | 64.8881 | 65.3469 | 65.8058 | 66.2646 | 66.7234 | 67.1823 | 67.6411 | 68.1 | 68.5588 | 69.0176 | 69.4765 | 69.9353 | 70.3941 | 70.853 | 71.3118 | 71.7707 | 72.2295 | 72.6883 | 73.1472 | 73.606 | 74.0649 | 74.5237 | 74.9825 | 75.4414 | 75.9002 | 76.359 | 76.8179 | 77.2767 | 77.7356 | 78.1944 | 78.6532 | 79.1121 | 79.5709 | 80.0298 | 80.4886 | 80.9474 | 81.4063 | 81.8651 | 82.3239 | 82.7828 | 83.2416 | 83.7005 | 84.1593 | 84.6181 | 85.077 | 85.5358 | 85.9946 | 86.4535 | 86.9123 | 87.3712 | 87.83 | 88.2888 | 88.7477 | 89.2065 | 89.6654 | 90.1242 | 90.583 | 91.0419 | 91.5007 | 91.9595 | 92.4184 | 92.8772 | 93.3361 | 93.7949 | 94.2537 | 94.7126 | 95.1714 | 95.6303 | 96.0891 | 96.5479 | 97.0068 | 97.4656 | 97.9244 | 98.3833 | 98.8421 | 99.301 | 99.7598
|  | 105 | 34.5224 | 34.9813 | 35.4401 | 35.8989 | 36.3578 | 36.8166 | 37.2755 | 37.7343 | 38.1931 | 38.652 | 39.1108 | 39.5697 | 40.0285 | 40.4873 | 40.9462 | 41.405 | 41.8638 | 42.3227 | 42.7815 | 43.2404 | 43.6992 | 44.158 | 44.6169 | 45.0757 | 45.5346 | 45.9934 | 46.4522 | 46.9111 | 47.3699 | 47.8287 | 48.2876 | 48.7464 | 49.2053 | 49.6641 | 50.1229 | 50.5818 | 51.0406 | 51.4995 | 51.9583 | 52.4171 | 52.876 | 53.3348 | 53.7936 | 54.2525 | 54.7113 | 55.1702 | 55.629 | 56.0878 | 56.5467 | 57.0055 | 57.4643 | 57.9232 | 58.382 | 58.8409 | 59.2997 | 59.7585 | 60.2174 | 60.6762 | 61.1351 | 61.5939 | 62.0527 | 62.5116 | 62.9704 | 63.4292 | 63.8881 | 64.3469 | 64.8058 | 65.2646 | 65.7234 | 66.1823 | 66.6411 | 67.1 | 67.5588 | 68.0176 | 68.4765 | 68.9353 | 69.3941 | 69.853 | 70.3118 | 70.7707 | 71.2295 | 71.6883 | 72.1472 | 72.606 | 73.0649 | 73.5237 | 73.9825 | 74.4414 | 74.9002 | 75.359 | 75.8179 | 76.2767 | 76.7356 | 77.1944 | 77.6532 | 78.1121 | 78.5709 | 79.0298 | 79.4886 | 79.9474 | 80.4063 | 80.8651 | 81.3239 | 81.7828 | 82.2416 | 82.7005 | 83.1593 | 83.6181 | 84.077 | 84.5358 | 84.9946 | 85.4535 | 85.9123 | 86.3712 | 86.83 | 87.2888 | 87.7477 | 88.2065 | 88.6654 | 89.1242 | 89.583 | 90.0419 | 90.5007 | 90.9595 | 91.4184 | 91.8772 | 92.3361 | 92.7949 | 93.2537 | 93.7126 | 94.1714 | 94.6303 | 95.0891 | 95.5479 | 96.0068 | 96.4656 | 96.9244 | 97.3833 | 97.8421 | 98.301 | 98.7598
|  | 104 | 33.5224 | 33.9813 | 34.4401 | 34.8989 | 35.3578 | 35.8166 | 36.2755 | 36.7343 | 37.1931 | 37.652 | 38.1108 | 38.5697 | 39.0285 | 39.4873 | 39.9462 | 40.405 | 40.8638 | 41.3227 | 41.7815 | 42.2404 | 42.6992 | 43.158 | 43.6169 | 44.0757 | 44.5346 | 44.9934 | 45.4522 | 45.9111 | 46.3699 | 46.8287 | 47.2876 | 47.7464 | 48.2053 | 48.6641 | 49.1229 | 49.5818 | 50.0406 | 50.4995 | 50.9583 | 51.4171 | 51.876 | 52.3348 | 52.7936 | 53.2525 | 53.7113 | 54.1702 | 54.629 | 55.0878 | 55.5467 | 56.0055 | 56.4643 | 56.9232 | 57.382 | 57.8409 | 58.2997 | 58.7585 | 59.2174 | 59.6762 | 60.1351 | 60.5939 | 61.0527 | 61.5116 | 61.9704 | 62.4292 | 62.8881 | 63.3469 | 63.8058 | 64.2646 | 64.7234 | 65.1823 | 65.6411 | 66.1 | 66.5588 | 67.0176 | 67.4765 | 67.9353 | 68.3941 | 68.853 | 69.3118 | 69.7707 | 70.2295 | 70.6883 | 71.1472 | 71.606 | 72.0649 | 72.5237 | 72.9825 | 73.4414 | 73.9002 | 74.359 | 74.8179 | 75.2767 | 75.7356 | 76.1944 | 76.6532 | 77.1121 | 77.5709 | 78.0298 | 78.4886 | 78.9474 | 79.4063 | 79.8651 | 80.3239 | 80.7828 | 81.2416 | 81.7005 | 82.1593 | 82.6181 | 83.077 | 83.5358 | 83.9946 | 84.4535 | 84.9123 | 85.3712 | 85.83 | 86.2888 | 86.7477 | 87.2065 | 87.6654 | 88.1242 | 88.583 | 89.0419 | 89.5007 | 89.9595 | 90.4184 | 90.8772 | 91.3361 | 91.7949 | 92.2537 | 92.7126 | 93.1714 | 93.6303 | 94.0891 | 94.5479 | 95.0068 | 95.4656 | 95.9244 | 96.3833 | 96.8421 | 97.301 | 97.7598
|  | 103 | 32.5224 | 32.9813 | 33.4401 | 33.8989 | 34.3578 | 34.8166 | 35.2755 | 35.7343 | 36.1931 | 36.652 | 37.1108 | 37.5697 | 38.0285 | 38.4873 | 38.9462 | 39.405 | 39.8638 | 40.3227 | 40.7815 | 41.2404 | 41.6992 | 42.158 | 42.6169 | 43.0757 | 43.5346 | 43.9934 | 44.4522 | 44.9111 | 45.3699 | 45.8287 | 46.2876 | 46.7464 | 47.2053 | 47.6641 | 48.1229 | 48.5818 | 49.0406 | 49.4995 | 49.9583 | 50.4171 | 50.876 | 51.3348 | 51.7936 | 52.2525 | 52.7113 | 53.1702 | 53.629 | 54.0878 | 54.5467 | 55.0055 | 55.4643 | 55.9232 | 56.382 | 56.8409 | 57.2997 | 57.7585 | 58.2174 | 58.6762 | 59.1351 | 59.5939 | 60.0527 | 60.5116 | 60.9704 | 61.4292 | 61.8881 | 62.3469 | 62.8058 | 63.2646 | 63.7234 | 64.1823 | 64.6411 | 65.1 | 65.5588 | 66.0176 | 66.4765 | 66.9353 | 67.3941 | 67.853 | 68.3118 | 68.7707 | 69.2295 | 69.6883 | 70.1472 | 70.606 | 71.0649 | 71.5237 | 71.9825 | 72.4414 | 72.9002 | 73.359 | 73.8179 | 74.2767 | 74.7356 | 75.1944 | 75.6532 | 76.1121 | 76.5709 | 77.0298 | 77.4886 | 77.9474 | 78.4063 | 78.8651 | 79.3239 | 79.7828 | 80.2416 | 80.7005 | 81.1593 | 81.6181 | 82.077 | 82.5358 | 82.9946 | 83.4535 | 83.9123 | 84.3712 | 84.83 | 85.2888 | 85.7477 | 86.2065 | 86.6654 | 87.1242 | 87.583 | 88.0419 | 88.5007 | 88.9595 | 89.4184 | 89.8772 | 90.3361 | 90.7949 | 91.2537 | 91.7126 | 92.1714 | 92.6303 | 93.0891 | 93.5479 | 94.0068 | 94.4656 | 94.9244 | 95.3833 | 95.8421 | 96.301 | 96.7598
|  | 102 | 31.5224 | 31.9813 | 32.4401 | 32.8989 | 33.3578 | 33.8166 | 34.2755 | 34.7343 | 35.1931 | 35.652 | 36.1108 | 36.5697 | 37.0285 | 37.4873 | 37.9462 | 38.405 | 38.8638 | 39.3227 | 39.7815 | 40.2404 | 40.6992 | 41.158 | 41.6169 | 42.0757 | 42.5346 | 42.9934 | 43.4522 | 43.9111 | 44.3699 | 44.8287 | 45.2876 | 45.7464 | 46.2053 | 46.6641 | 47.1229 | 47.5818 | 48.0406 | 48.4995 | 48.9583 | 49.4171 | 49.876 | 50.3348 | 50.7936 | 51.2525 | 51.7113 | 52.1702 | 52.629 | 53.0878 | 53.5467 | 54.0055 | 54.4643 | 54.9232 | 55.382 | 55.8409 | 56.2997 | 56.7585 | 57.2174 | 57.6762 | 58.1351 | 58.5939 | 59.0527 | 59.5116 | 59.9704 | 60.4292 | 60.8881 | 61.3469 | 61.8058 | 62.2646 | 62.7234 | 63.1823 | 63.6411 | 64.1 | 64.5588 | 65.0176 | 65.4765 | 65.9353 | 66.3941 | 66.853 | 67.3118 | 67.7707 | 68.2295 | 68.6883 | 69.1472 | 69.606 | 70.0649 | 70.5237 | 70.9825 | 71.4414 | 71.9002 | 72.359 | 72.8179 | 73.2767 | 73.7356 | 74.1944 | 74.6532 | 75.1121 | 75.5709 | 76.0298 | 76.4886 | 76.9474 | 77.4063 | 77.8651 | 78.3239 | 78.7828 | 79.2416 | 79.7005 | 80.1593 | 80.6181 | 81.077 | 81.5358 | 81.9946 | 82.4535 | 82.9123 | 83.3712 | 83.83 | 84.2888 | 84.7477 | 85.2065 | 85.6654 | 86.1242 | 86.583 | 87.0419 | 87.5007 | 87.9595 | 88.4184 | 88.8772 | 89.3361 | 89.7949 | 90.2537 | 90.7126 | 91.1714 | 91.6303 | 92.0891 | 92.5479 | 93.0068 | 93.4656 | 93.9244 | 94.3833 | 94.8421 | 95.301 | 95.7598
|  | 101 | 30.5224 | 30.9813 | 31.4401 | 31.8989 | 32.3578 | 32.8166 | 33.2755 | 33.7343 | 34.1931 | 34.652 | 35.1108 | 35.5697 | 36.0285 | 36.4873 | 36.9462 | 37.405 | 37.8638 | 38.3227 | 38.7815 | 39.2404 | 39.6992 | 40.158 | 40.6169 | 41.0757 | 41.5346 | 41.9934 | 42.4522 | 42.9111 | 43.3699 | 43.8287 | 44.2876 | 44.7464 | 45.2053 | 45.6641 | 46.1229 | 46.5818 | 47.0406 | 47.4995 | 47.9583 | 48.4171 | 48.876 | 49.3348 | 49.7936 | 50.2525 | 50.7113 | 51.1702 | 51.629 | 52.0878 | 52.5467 | 53.0055 | 53.4643 | 53.9232 | 54.382 | 54.8409 | 55.2997 | 55.7585 | 56.2174 | 56.6762 | 57.1351 | 57.5939 | 58.0527 | 58.5116 | 58.9704 | 59.4292 | 59.8881 | 60.3469 | 60.8058 | 61.2646 | 61.7234 | 62.1823 | 62.6411 | 63.1 | 63.5588 | 64.0176 | 64.4765 | 64.9353 | 65.3941 | 65.853 | 66.3118 | 66.7707 | 67.2295 | 67.6883 | 68.1472 | 68.606 | 69.0649 | 69.5237 | 69.9825 | 70.4414 | 70.9002 | 71.359 | 71.8179 | 72.2767 | 72.7356 | 73.1944 | 73.6532 | 74.1121 | 74.5709 | 75.0298 | 75.4886 | 75.9474 | 76.4063 | 76.8651 | 77.3239 | 77.7828 | 78.2416 | 78.7005 | 79.1593 | 79.6181 | 80.077 | 80.5358 | 80.9946 | 81.4535 | 81.9123 | 82.3712 | 82.83 | 83.2888 | 83.7477 | 84.2065 | 84.6654 | 85.1242 | 85.583 | 86.0419 | 86.5007 | 86.9595 | 87.4184 | 87.8772 | 88.3361 | 88.7949 | 89.2537 | 89.7126 | 90.1714 | 90.6303 | 91.0891 | 91.5479 | 92.0068 | 92.4656 | 92.9244 | 93.3833 | 93.8421 | 94.301 | 94.7598
|  | 100 | 29.5224 | 29.9813 | 30.4401 | 30.8989 | 31.3578 | 31.8166 | 32.2755 | 32.7343 | 33.1931 | 33.652 | 34.1108 | 34.5697 | 35.0285 | 35.4873 | 35.9462 | 36.405 | 36.8638 | 37.3227 | 37.7815 | 38.2404 | 38.6992 | 39.158 | 39.6169 | 40.0757 | 40.5346 | 40.9934 | 41.4522 | 41.9111 | 42.3699 | 42.8287 | 43.2876 | 43.7464 | 44.2053 | 44.6641 | 45.1229 | 45.5818 | 46.0406 | 46.4995 | 46.9583 | 47.4171 | 47.876 | 48.3348 | 48.7936 | 49.2525 | 49.7113 | 50.1702 | 50.629 | 51.0878 | 51.5467 | 52.0055 | 52.4643 | 52.9232 | 53.382 | 53.8409 | 54.2997 | 54.7585 | 55.2174 | 55.6762 | 56.1351 | 56.5939 | 57.0527 | 57.5116 | 57.9704 | 58.4292 | 58.8881 | 59.3469 | 59.8058 | 60.2646 | 60.7234 | 61.1823 | 61.6411 | 62.1 | 62.5588 | 63.0176 | 63.4765 | 63.9353 | 64.3941 | 64.853 | 65.3118 | 65.7707 | 66.2295 | 66.6883 | 67.1472 | 67.606 | 68.0649 | 68.5237 | 68.9825 | 69.4414 | 69.9002 | 70.359 | 70.8179 | 71.2767 | 71.7356 | 72.1944 | 72.6532 | 73.1121 | 73.5709 | 74.0298 | 74.4886 | 74.9474 | 75.4063 | 75.8651 | 76.3239 | 76.7828 | 77.2416 | 77.7005 | 78.1593 | 78.6181 | 79.077 | 79.5358 | 79.9946 | 80.4535 | 80.9123 | 81.3712 | 81.83 | 82.2888 | 82.7477 | 83.2065 | 83.6654 | 84.1242 | 84.583 | 85.0419 | 85.5007 | 85.9595 | 86.4184 | 86.8772 | 87.3361 | 87.7949 | 88.2537 | 88.7126 | 89.1714 | 89.6303 | 90.0891 | 90.5479 | 91.0068 | 91.4656 | 91.9244 | 92.3833 | 92.8421 | 93.301 | 93.7598